## New Wateryard (hidden)
BILL OF QUANTITIES
South Sudan Enhancing Community Resilience and Local Governance Project (ECRP)
Project Description: Wungok Village GPS : N=10.07358889, E=29.89319444 (Wungok Boma)-Werthen Payam, Abouny Village GPS: N=9.939001, E=29.825724 (Wunkur Boma)-Aliiny Payam ; Ayija Village GPS: N=9.88216667, E=29.94313889 (Akotweng Boma)-Nyiel Payam; Drilling and construction of 3 new water yards installed with solar panels and submersible pump;
Name of Bidder:
I | Description | Unit | Quantity required for project | Unit Cost [USD] | Total cost (USD)
BILL NO 1 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT |  |  |  | 0
1 | SOLAR SYSTEM
1.1 | Supply and installtion of a Dayliff or Lorentz solar system providing at least 36m3/day considering 6 hours of sunshine. The system shall comprise of a submersible pump and well probe, float switch, smart PSU with wireless data connect, PV Disconnect, surge protector and lighting arrestor with a minimum of 1 piece of 8‐foot copper‐plated grounding rod. Design of the solar system needs to be inspected and validated by IOM prior to procurement and installation. | LS | 1 |  | 0
2.1 | Supply and install of a parallel series solar pannels certified to ISO, IEC 61215 and 61730 (TÜV Rheinland) and CE oversized by 1.2 to 1.3 times the motor size. The solar panels shall be mounted facing North and a tilt angle of 7deg, mounted onto a fabricated frame above the storage tanks. | LS | 1 |  | 0
3 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT
3.1 | Horizontal installation of 3 flow meters, at the inlet of the storage, and 1 per water kiosk. | pcs | 3 |  | 0
3.2 | Supply and installation of 6.0 metre high metalic stand tower for tank, evenly coated with a layer of anti-oxide paint and overlayed with an additional coating of grey/silver paint and fitted with a hooped cat-ladder, top walkways of 2.1mm thickness and safety hand railings. Tower to comply to manufacturing standards: Dead/Live load analysis to BS 6399. Wind load analysis to CP3 ch V 1972. Structural steel work to BS 5950 Part 1 1990. | LS | 1 |  | 0
3.3 | Supply and installation of 2 PVC high quality water tank of 5,000 liter each (Toptank recommended). | pcs | 2 |  | 0
3.4 | Supply and installation of 2-1/2'' HDPE underground distribution and uPVC, PPR class 10 above ground pipeline and fittings. | m | 300 |  | 0
4 | WATER YARD SITE LAYOUT
4.1 | The borehole shall be fitted with a well head casted in a concrete platform of minimum 0.3m height and protected by a man hole with a cast iron trap fitted with a lockable system. | LS | 1 |  | 0
4.2 | Levelling of the site and laying a 300mm thickness well compacted murram of 60% minimum aggregate approved by the IOM Supervisor prior to installation. | LS | 1 |  | 0
5 | REPORTING
5.1 | Submit well completion report as per IOM template, including results of water quality analysis. | No | 1 |  | 0
BILL SUMMARY
BILL NO 1 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT | Unit | 3 | 0 | 0
|  | GRAND TOTAL |  |  | 0

## Water Yard Rehabilitation (hidden)
BILL OF QUANTITIES
South Sudan Enhancing Community Resilience and Local Governance Project (ECRP)
Project Description: Abon 2 Village GPS: N=9.918025, E=29.98141389 (Waukok Boma)-Pariang Payam, - Drilling and rehabilitation of existing water yard installed with solar panels and submersible pump, Pariang County, Unity State
Name of Bidder:
I | Description | Unit | Quantity | Unit Cost | Total cost
BILL NO. 1 | PRELIMINARIES |  |  |  | 0
Notes:
| All the Bidders are requested to refer "Pricing Preamble and notes below" and works items of this Bills of Quantities shall be priced to fulfill the requirements there-in. Also see that no page or items are missing prior to pricing of this bill of quantities. | Note
| A list of typical general items are given below. However, the Bidder is requested to price only those items that may affect this Contract. | Note
| If no price has been stated against any item hereunder, the Contractor shall not be entitled to claim any money for such items even though he is obliged to execute the work or provide services described therein. Preliminary items priced by the Tenderer are deemed to include the cost of unpriced items. | Note
| Cost and expenses in connection with any other preliminary item which is not listed below, but is necessary for the due completion of works, is deemed to be included in the tender rates. | Note
1.1 | Site Facilities |  |  |  | 0
1.1.1 | Mobilization and demobilization from the site including all requirements of Guideline GHS12 - Site Establishment - Preparation works, protection of existing structures, materials and items, site boundaries, information board, office and welfare facilities, storage sites, generator, site reinstatement, safety, and security | 1 | Lump Sum |  | 0
1.1.2 | Fabricate a metal visibility plate 100 x 80 mm to be wall mounted. Art work of name board will be issued by IOM | 1 | each |  | 0
1.2 | Sites Operations |  |  |  | 0
1.2.1 | Allow for setting out of works in accordance with drawings; liaise with client to establish exact boundaries and other written information given by the Engineer and obtain written approval from the relevant government authorities for setting out, street and building lines before commencements of construction; Checking of any setting out or of any line or level by the Engineer shall not in any way relieve the Contractor of his responsibility for the accuracy thereof. | 1 | Lump Sum |  | 0
1.2.2 | Tools, plant, and scaffolding | 1 | Lump Sum |  | 0
1.2.3 | Allow for providing all necessary safety measures to workmen (provision for proper usage of Personal protective equipment (PPE)). | 1 | Lump Sum |  | 0
1.3 | Insurances, Bonds & Fees |  |  |  | 0
1.3.1 | Allow for Contractor's All Risk Insurance Policy, including third party liability and from the starting date until the defects liability certificate has been issued, the risks of personal injury, death, and loss of or damage to property (including, without limitation, the works, plant, materials, and equipment) which are not employers risk but are contractors risk Allow for insurance against claims for worker's compensation. Engineer's and Consultant's representatives, shall be included in the Insurance Policy. Allow for insurance against loss or damage to the works, adjacent structures, any existing overhead and/or underground services that may cause damages during the construction | 1 | Lump Sum |  | 0
BILL NO. 4 | REHABILITATION OF EXISITING WATER YARD |  |  |  | 0
4.1 | Supply and Installation of solar pump, solar panels and accessories | Unit | Quantity | Unit Rate | 0
4.1.1 | Supply and install Deep Well Submersible Pump, 4" 2 HP, 220V, 35 GPM, 400 ft Max, long life, to provide at least 48m3/day considering 8 hours of sunshine and a total dynamic head of 90m. The system shall comprise of control panel, submersible cable of at least 110m, float switch, UPVC Riser pipes and adaptor set, surge protector and lighting arrestor with a minimum of 1 piece of 8‐foot copper‐plated grounding rod. Design of the solar system needs to be inspected and validated by IOM prior to procurement and installation. | LS | 1 |  | 0
4.1.2 | Supply and install in a parallel series solar pannels 300 W and above, certified to ISO, IEC 61215 and 61730 (TÜV Rheinland) and CE oversized by 1.2 to 1.3 times the motor size. The solar panels shall be mounted facing North and a tilt angle of 7deg, mounted onto a fabricated frame above the storage tanks. | LS | 1 |  | 0
4.2 | Water tank rehabilitation, Water distribution network and rehabilitation of existing water points. |  |  |  | 0
4.2.1 | Horizontal installation of 4 flow meters, at the inlet of the storage, and 1 per water stand tap station | pcs | 4 |  | 0
4.2.2 | Repair and modify the existing 6.6 metre high metalic stand tower, including providing metallic solar panels carrier welded to the existing stand tower at least 1m above water tank, ensuring strong bracings and all necessary support to resist effect of wind force. Ensure that the solar panel carrier is inclined and oriented appropariately. Conduct thorough check on the exisiting 20M3 metallic circular tank against any leakage, evenly coated with a layer of anti-oxide zinc phosphate paint and overlayed with an additional coating of grey/silver paint and fitted with a hooped cat-ladder, top walkways of 2.1mm thickness and safety hand railings. | LS | 1 |  | 0
4.2.3 | Supply and installation of 2-11/2'' HDPE underground distribution and uPVC, PPR class 10 above ground pipeline and fittings. | m | 400 |  | 0
4.2.4 | Rehabilitation of 4 water points with 3 Talbot Talflow self closing taps each in hollow block and concrete masonry including construction of a drainage channel and a soak away pit. | pcs | 4 |  | 0
4.3 | SITE LAYOUT |  |  |  | 0
4.3.1 | The borehole shall be fitted with a pedestal stand casted raised at least 0.7m in a concrete platform of minimum 0.3m thick and protected by a man hole with a cast iron trap fitted with a lockable system. The well must have provision for deep meter hole to check static water level and depth of BH | LS | 1 |  | 0
4.3.2 | Levelling of the site and laying with well compacted murram of 60% minimum aggregate laid at interval not exceeding 100mm thick until 300mm thickness is achieved, as approved by the IOM Supervisor prior to installation. | LS | 1 |  | 0
4.3.3 | Supply and installation of a fence 8m x 8m to secure the solar system and the borehole (if feasible). The fence shall be constructed using Y shaped circular steel hollow section tubes of 50mm diameter by 3mm thickness or casted in a concrete (1:2:4) foundation (W: 0.3 X L: 0.3 X H: 0.7 m). The top part of the pole shall be welded with V-shaped of 500mm length and installed with razor wire of 0.9m diameter. The height of the pole above ground shall be determined by the height of the chain link supplied but should be of minimum 1.9m. The poles shall be installed 1.5 meters apart and reinforced using 3 lines of tension wire. An apron of 200mm wide shall be casted all round along the fence perimeter | LS | 1 |  | 0
4.3.4 | Installation of a gate frame constructed with 2 pieces of 100mm x 100mm x 3mm (4x4 inch) hollow section frame, each supported by an additional member placed at 60deg angle from the vertical pole. The gate itself shall be constructed with 60mm x 60mm x 3mm hollow sections shutter frame and covered with wire mesh. | LS | 1 |  | 0
4.3.5 | Fence and gate shall be evenly painted with a single layer of anti-oxyde paint and overlayed with an additional coating of grey/silver paint. | LS | 1 |  | 0
4.3.6 | Supply and installation of 2 modular all-in-one solar street lights, attached directly onto the solar frames and secured by razor wire. | pcs | 2 |  | 0
BILL SUMMARY
BILL NO. 4 | REHABILITATION OF EXISITING WATER YARD | Unit | 1 | 0 | 0
|  | GRAND TOTAL |  |  | 0

## New Elavated water tank
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURES WORKS- DHAGAX-DHEER TOG-DHEER- SOMALILAND.
BoQs of Elevated Water Tank 50m3 (12m high)
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | Elevated Water Tank 50m3 (12m high)
1 | Foundation
1.1 | Excavation: General excavation works for the column's foundations, depth up to 1500mm in all type of soil | m3 | 39.89 |  | 0
1.2 | Lean concrete (2000 x 2000mm, thickness 50mm): lean concrete, mix 1:4:8, ready to receive the the column's foundations | m3 | 1.2 |  | 0
1.3 | Foundations (1400 x 1400mm, thickness 600mm): reinforced concrete class 20 (nominal mix 1:2:4) with Y12 at column bases | m3 | 7.056 |  | 0
2 | Columns and Beams
2.1 | Columns (section: 300mmx 300mm): reinforced concrete mix 1:2:4, with high yield twisted rebar of Y12 and R6 for stirrups @200mm c/c | m3 | 5.83 |  | 0
2.2 | Beam (section 300x450mm), concrete class 20,nominal mix 1:2:4) with Y16 rebar and R8 for beam links | m3 | 9.32 |  | 0
3 | Storage tank (RC slabs and RC walls)
3.1 | Tank slab: (3400 x 6400mm, thickness 1500mm): reinforced concrete class 25 ( nominal mix 1:2:3) complete with water proofing, 12mm dia high yield square twisted bars for tank base slab | m3 | 3.264 |  | 0
3.2 | Water bar: 200mm water bar | Lm | 17 |  | 0
3.3 | Walls: (thickness 12mm and height of 2000mm) reinforced concrete class 25 ( nominal mix 1:2:3) complete with water proofing; 12mm high yield square twisted bars for tank walls | m3 | 3.384 |  | 0
3.4 | Cover slab: (4400 x 4400mm, thickness 150mm): reinforced concrete class 20 (nominal mix 1:2:4), 12mm high yield square twisted bars for tank cover slab | m3 | 1.984 |  | 0
4 | Inspection manhole and fittings
4.1 | Inspection manhole (600mm x 600mm): Reinforced concrete 50mm thick with BS mesh A142, bent up round iron bars handle and 50x50x3mm, using of Y12 HY Square twisted bars at man hole corners | unit | 0.02 |  | 0
4.2 | BS mesh A142 for manhole cover | m2 | 0.4 |  | 0
4.3 | 50x50x3mm L angle plates | lm | 16 |  | 0
4.4 | Fittings: supply and install all fittings for inlet, distribution and trucking outlets and overflow | LS | 1 |  | 0
4.5 | Ladder (500mm width,13m length): Supply and install a metallic ladder, including all anchorage points | Unit | 1 |  | 0
Total of Bill NO. A, BoQs of BoQs of Elevated Water Tank, carried forward to summary |  |  |  |  | 0

## Borehole supplies
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURE WORKS- DHAGAX-DHEER, TOG-DHEER- SOMALILAND.
BoQs PROPOSED BOREHOLE SUPPLIES
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | BOREHOLE SUPPLIES
A 1 | Foundation
A 1.1 | Procurement & Installation of Submersible pump, Grundfos SP17-20 Rp2 with 15kW motor, with 405m head with matching cut-off electrodes, drop cables control panel, all accessories included | Pcs | 1 |  | 0
A 1.2 | Provision and installation of GI 2” riser main pipe for the borehole with complete fittings | Pcs | 67 |  | 0
A 1.3 | Gate valves and control panel for the pump | Pcs | 1 |  | 0
C 1.1 | Allow a provisional sum of water meter readers in the borehole outlet | No. | 1 |  | 0
C 1.2 | Disinfection and chlorination of the borehole | Item | 1 |  | 0
C 1.3 | Construct mass concrete of 1:2:4 mixing ratio for the head of wall 1 m above the ground and cover the hole | m³ | 1 |  | 0
C 1.4 | Allow provisonal sum of gantry at borehole site | No | 1 |  | 0
Total of Bill NO. A, BoQs of Borehole supplies, carried forward to summary |  |  |  |  | 0

## Distribution Piping
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURE WORK- DHAGAX-DHEER, TOG-DHEER- SOMALILAND.
BoQs PROPOSED BOREHOLE SUPPLIES
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | BOREHOLE SUPPLIES
1 | Foundation
1.1 | Excavation of a trench (0.4m wide x 0.7m deep) for a total length of 1.5 km from borehole to the town | m3 | 315 |  | 0
1.2 | Supply & Install PVC heavy gauge Ø 2", each length 6m for delivery including all necessary fittings from borehole to the town, installed over a sand bed 7 cm thick and covered with sand for a minimum thickness of 10 cm. | M.L. | 1500 |  | 0
1.3 | Refill the pipeline trench with duly compacted soil free of relicts of excavation | M.L. | 1500 |  | 0
1.4 | Demarcation and layouts preparation | LS | 1 |  | 0
1.5 | Construction of chamber control Box (50x50x50cm) | Sum | 8 |  | 0
1.5 | Testing the system | Sum | 1 |  | 0
1.6 | Supply of 2 inch uPVC pressure pipes for supplying water from tank to the town also connect to animal trough and water kiosks | Pcs | 250 |  | 0
1.7 | Supply of all the fittings including elbows, tees, unions, gate valves, flow meters etc | LS | 1 |  | 0
Total of Bill NO. A, BoQs of Piping, carried forward to summary |  |  |  |  | 0

## Water Kiosks
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURES WORKS- DHAGAX-DHEER, TOG-DHEER- SOMALILAND.
BoQs of PROPOSED BOREHOLE WATER KIOSKS
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | WATER KIOSKS
A 1 | Construction of water Kiosks
1.1 | Clearing of the site to remove top soil and other rubbish materials to an average depth of 200 mm. | m2 | 40 |  | 0
1.2 | Levelling and grading for foundation to a depth not exceeding 500mm starting from reduced level. | m3 | 18 |  | 0
1.3 | Backfill with selected material, well rammed in layers of 200mm thick and compacted at dry density and optimum moisture content to achieve 95% standard proctor. | m3 | 7 |  | 0
1.4 | Cart away excavated material. | m3 | 15 |  | 0
1.5 | 10cm thick C-20 mass concrete in water point base and on the surface of the hard core | m2 | 12 |  | 0
1.6 | 200mm Solid block or equivalent stone masonry water point wall grouted and filled with 1:3 mortar | m3 | 28 |  | 0
1.7 | Pointing stone masonry wall of water point with rich (1:3) mortar | m2 | 10 |  | 0
1.8 | 100mm cement screed on top of the water point and make a platform. | m2 | 10 |  | 0
2 | PIPE & ACCESSORIES
2.1 | PPR pipe 1'' | ml | 12 |  | 0
2.2 | Elbow 90 deg. dia. 1" | No. | 8 |  | 0
2.3 | Reducer dia. 1 ½"x1" | No. | 2 |  | 0
2.4 | Tee dia. 1” | No. | 2 |  | 0
2.5 | Faucet dia.1" | No. | 8 |  | 0
2.6 | Gate Valve dia. 1" | No. | 1 |  | 0
2.7 | Nipples dia 1 " | No. | 1 |  | 0
2.8 | Union dia 1 " | No. | 1 |  | 0
2.9 | Visibilaty bill board (1.2mx1m) with a 11/2 GI pipe legs and length of 3m the GI pipe should fix concrete at the bottom. | LS | 1 |  | 0
2.1 | Adapter PPR 1" | No. | 5 |  | 0
Sub-total for One Kiosk
Total of Bill NO. A, BoQs of BoQs of Water Kiosks, carried forward to summary |  |  |  |  | 0

## Animal Troughs
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURE WORKS- DHAGAX-DHEER, TOG-DHEER- SOMALILAND.
BoQs of PROPOSED CONSTRUCTION OF ANIMAL TROUGH
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | CONSTRUCTION OF ANIMAL TROUGH
A 1 | Sub structure works
A 1.1 | Excavation Works:
A 1.2 | Excavate 80m long trench with average depth of 400mm into the rock from the elevated water tank to the water point | Item | 1 |  | 0
A 1.3 | Pipes and Accessories |  |  |  | 0
A 1.4 | PVC pressure pipe with 3" diameter | M | 60 |  | 0
A 1.5 | Elbow 90 deg. dia. 3" | No | 2 |  | 0
A 1.6 | Reducer dia. 2 ½"x3" | No | 1 |  | 0
A 1.7 | Union diam 3" | No | 3 |  | 0
A 1.8 | Nipples 3" | No | 1 |  | 0
A 1.9 | Adaptor dia 3" | No | 2 |  | 0
A 1.10 | Socket dia 3" | No | 2 |  | 0
A 1.11 | Gate valve diam 3" | No | 1 |  | 0
A 1.2 | Excavate 400mm thick to the rock to a depth of 500mm below the ground level | CM | 6.6 |  | 0
A 1.13 | Place 50mm thick plain concrete for blind in 1:4:8 mix ratio | SM | 13.2 |  | 0
A 1.14 | 200mm thick VRC foundation concrete in 1:2:4 mix ratio | CM | 2.64 |  | 0
A 1.15 | 3Y10 for foundation reinforcement at 200mm C/C | Kg | 61.1111 |  | 0
A 1.16 | Y10 reinforcement at 250mm C/C | Kg | 49.2593 |  | 0
A 1.17 | Y8 reinforcement to the walling at 150mm C/C | Kg | 203.3778 |  | 0
A 1.18 | 200mm thick VRC walling concrete in 1:2:4 mix ratio | CM | 5.68 |  | 0
A 1.19 | An item for walling formwork including marine ply and timber bracing | Item | 1 |  | 0
A 2.0 | 150mm thick mass concrete aprone in 1:3:6 mix on the longer side walling of the water trough extended 3m from the wall on both sides with hardcore support on the bottom | LS | 1 |  | 0
A 2.1 | Backfilling to the tench | CM | 1.98 |  | 0
A 2.3 | 1:3 C/S mortor to 30mm thick wall plaster inside-out | SM | 37 |  | 0
A 1.2 | Total for construction of one animal trough |  |  |  | 0
| Total for construction of two animal trough |  |  | 2 | 0
Total of Bill NO. A, BoQs of animal trough, carried forward to summary |  |  |  |  | 0

## Solar Installation
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURES WORKS- DHAGAX-DHEER TOG-DHEER- SOMALILAND.
BoQs of PROPOSED SOLAR PROCUREMENT,DELIVERY & INSTALLATION
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | SOLAR PROCUREMENT,DELIVERY & INSTALLATION
A 1 | SITE PREPARATION
1.1 | Mobilization of staff, equipment and materials to site | Item | 1 |  | 0
1.2 | INVT On Grid Inverter (BG22KTR) EU Standard, Output Power: 18000W, Output Voltage: 380V AC, Warranty: 1 years | No | 1 |  | 0
1.3 | Supply and install (Mono 450W solar panel) 16pcs per string, total 3 strings Power: 450W Voltage: 49V, Weight:25KG Size:2265*1260*35mm, Application Class: A Warranty: 5 years | No | 50 |  | 0
1.4 | Supply & installation (Accessories) DC Combiner Box, 6 Input 1 output Warranty: 1 years | Unit | 1 |  | 0
1.5 | PV Cable, PV 4 mm2 | M | 450 |  | 0
1.6 | Accessories, Mc4, Cable tie, Autoswitch and etc. | Unit | 1 |  | 0
1.7 | B Meters DN40 water meter | No | 1 |  | 0
1.8 | Procure and install Aluminum Roof Mounting Structure frames-Imported standard not local made frames with 30cmX30cm and 50cm depth plain concrete foundation as per intruction of Engineer | LS | 1 |  | 0
Total of Bill NO. A, BoQs of Solar installations, carried forward to summary |  |  |  |  | 0

## Caretaker room
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURE WORKS- DHAGAX-DHEER, TOG-DHEER- SOMALILAND.
BOQ FOR THE CONSTRUCTION WORKS:
CONSTRUCTION OF CARETAKER ROOM, SOLAR ROOM 4x4x1.5 meters
#. | Description of activity | Unit | QTY | Rate in USD | Amount in USD
B. | Caretaker room
6 | Sub structure works
6.1 | Excavation of foundation trench 0.4m wide and 0.8m depth.B8:E18A2B8:E21B8:E17B8:E16 | m³ | 7.36 |  | 0
6.2 | Plain concrete in 50 mm thick blinding layer (1:3:6 mix) under the foundation wall. | m³ | 0.46 |  | 0
6.3 | Rubble stone foundation wall in cement & sand mortar 1:6 (1.0 m x 0.4m wide) min. 35cm above ground level. | m³ | 9.2 |  | 0
6.4 | R.C (1:2:4 mix) in ground beam (0.4m x0.20m ), with 8N0. Y14 re-bars & R6 links @ 200 mm c/c. | m³ | 1.84 |  | 0
6.5 | 20 cm thick stone hard-core filling well compacted and levelled. | m³ | 4.4 |  | 0
| Sub total - 1 |  |  |  | 0
7 | Superstructure works including conc. floor slab
7.1 | Mass concrete (1:3:6 mix ) in conc. floor slab 10cm thick. | m³ | 2.2 |  | 0
7.2 | Masonry cement blocks walling, 20cm thickness bedded and jointed with cement sand mortar 1:4 proportion ratio. Face wall should be plumb. Corner cement block should be good dressed and jointed to correct angles. All gaps in between cement blocks should be filled with cement sand mortar well mixed also wall should be kept moist for a period at least 10 days minimum, and be protected from sun. | m² | 78.2 |  | 0
7.3 | Masonry cement blocks ventilation hollow blocks walling, 20cm thickness bedded and jointed with cement sand mortar 1:4 proportion ratio. Face wall should plumb. Corner cement block should be good dressed and jointed to correct angles. All gaps in between cement blocks should be filled with cement sand mortar well mixed also wall should be kept moist for a period at least 10 days minimum, and be protected from sun | m² | 8 |  | 0
7.4 | R.C (1:2:4 mix) in above the doors & windows conc. ring beams 15 cm depth, each with 6N0. Y14 re-bars & R6 links @ 250 mm c/c. | m³ | 1.116 |  | 0
7.5 | R.C (1:2:4 mix) top tie beam conc. ring beams 30 cm depth, and 20cm wide, each with 6N0. Y14 re-bars & R6 links @ 250 mm c/c. | m³ | 1.116 |  | 0
7.6 | RCC (1:2:4) Columns of 20cmx20cm with reinforced No. 4 iron bars of diameter Ø 14mm | m³ | 1.024 |  | 0
7.7 | Constructing of R.C (1:2:4 Mixing ratio) floor slab of 0.1m thick for the solar room with Ø 12mm & 10mm main bars and 8mm distribution bars both ways at top and bottom and distanced 150mm c/c N.B The slab should mixed by machine, also it has to be kept moist and watered for a period of minimum 3 weeks and protect from sun | m³ | 2.2 |  | 0
7.8 | Constriction of 1:2:4 mixing ratio concrete at front of the generator house | m³ | 0.99887 |  | 0
7.9 | Construction of ceramic floor tiling for pavement of the caretaker room. The work consist providing of ceramic floor tile connected and jointed with cement sand mortar of 1:2 mixing ratio | m² | 14 |  | 0
7.1 | Construction wall skirt tiling for internal wall of the caretaker, by ceramic wall skirting tile connected and jointed with cement sand mortar of 1:2 mixing ratio | m | 4.05 |  | 0
| Sub total - 2 |  |  |  | 0
8 | Roofing
8.1 | Construction of gobble end GI sheet roof of 3m long and 1m wide with wooden trusses of height 1.0m made by timber of cross section 0.08mx0.04m and double tie beam made by timber of cross section 0.10mx0.025m, and wooden battens of 0.05mx0.05m. | m² | 22.8 |  | 0
8.2 | Construction of decorated ceiling board to the caretaker room with supporting wooden frame of 0.04mx0.04m distanced each to other 0.62m both side. N.B. Note that this ceiling is included also the outside projection of the room | m² | 22 |  | 0
| Construction of 20cm fascia board | m | 19.2 |  | 0
| Sub total - 3 |  |  |  | 0
9 | Plastering and other finishing
9.1 | Construction of external & internal plastering, 25mm thick, for all constructed wall surfaces by cement / sand mix 1:5, with wood float finish. | m² | 156 |  | 0
9.2 | Apply two coats whitewashing paint to all wall surfaces, reinforced concrete and pillars. | m² | 156 |  | 0
9.3 | Apply two coats distemper paint to all wall surfaces, reinforced concrete and pillars. | m² | 156 |  | 0
| Sub total - 4 |  |  |  | 0
10 | Gate, doors & Windows and other works
10.1 | Provide and fix 2.2m height and 2.34m wide steel doors for the caretaker room of steel hollow box of 40mmx40mmx2mm and decorated by steel hollow box of 25mmx25mmx1mm distanced each to other not more than 20cm c/c; covered to the bottom part by GI sheets of 1.5mm thick fixed with continuous weld. The rate shall include all fittings, fixtures and three coat of approved quality of anti-rust paint. | Item | 1 |  | 0
10.2 | Provide and fix new 1.0mx1.0m steel windows with required protection bars and insects net system and all required fittings of . | Item | 2 |  | 0
| Sub total - 5 |  |  |  | 0
11 | Electricity
11.1 | Provide and fix adequate electrical wiring system inside of the wall with PVC pipes, Provide also 4 sockets and four of 20W fluorescent lamps for room. Also one socket and one incandescent lamp . Finally supply and fix Main automatic switch board. | lum | 1 |  | 0
| Sub total - 6 |  |  |  | 0
| Total for construction caretaker room or Solar storage room |  |  |  | 0
Note on A3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is a construction and not a rehabilitation. Would be better if cost could be pegged at about $3.5K

## Solar fencing
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURE WORKS- DHAGAX-DHEER, TOG-DHEER- SOMALILAND.
BoQs of PROPOSED SOLAR FENCE AND GATE
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | FENCE AND GATE
A 1 | GATE
1.1 | The contractor will provide all material and construct a steel gate maesuring approximately 4500x2100m gate. Given the location and site conditions, the contractor is advised to make a physical assesment of the site before tendering | No | 1 |  | 0
1.2 | Excavate for column pads, depth not exceeding 1m and of 0.5 x 0.5 mm width commencing at the original ground level, and cart away to spoil as directed | M3 | 0.5 |  | 0
2 | Reinforced Concrete using 3/4 + 1/2" mix machine crushed Ballast in:
2.1 | Vibrated reinforced concrete (class 25) column base, 350mm deep | M3 | 0.05 |  | 0
2.2 | Assorted high tensile twisted steel reinforcement bars to B.S 4446. | KG | 20 |  | 0
2.3 | Sawn formwork to vertical sides of the columns | M2 | 10 |  | 0
2.4 | G.I CHS Columns | No | 2 |  | 0
2.5 | Supply and fix single leaf steel gate size 1500 x 2100mm high CHS poles and heavy duty wire mesh fixed onto the concrete columns using heavy duty steel pin hinges; with all fastening accessories including all cutting welding, grinding and priming with one coat of grey oxide fixing. The gate should also have peep holes of not more tha 25mm dia with a slilding door. It should also have 2 locking mechanisms, top and bottom. | No | 1 |  | 0
A 2 | FENCE
3 | The contractor is reminded to include in his pricing, the cost of supply, cutting, waste and erection and all other necessary fittings including welding lugs or fishtailing onto the 50x50x6mm angle bars. Angle bars and the necessary fixing and anchorage to be treated as described in the specifications. Fence construction should be according to BS 1722-Part 10
3.1 | Clear the perimeter of the fencing area of all bushes scrubs and obstructions | M2 | 24 |  | 0
3.2 | Excavate 300x300x500 deep holes to receive mass concrete (1:3:6)bases as shown in the drawings. | M3 | 0.6 |  | 0
3.3 | Supply 50x5mm CHS welded posts with ends closed as shown in the drawings, bottom end fixed with 100x100mmx3mm plate and bedded in mass concrete.The post to be 2100mm high from ground level to the top. Allow for drlling 7No holes as shown. | No | 13.33 |  | 0
3.4 | Extra Over 50x5mm posts for bracing on either side every fourth intermediate post and all corner posts. | No | 3.33 |  | 0
4 | Mass Concrete Mix 1:3:6/20mm using 3/4 Local Ballast in:
4.1 | Supply all materials and cast 0.3m diameter x 0.6m depth mass concreteclass Q (1:3:6) to concrete the 50mm dia. CHS poles while ensuring they remain plumb 600mm deep below the ground level and 2500mm (2.5m) above ground level. | M3 | 0.6 |  | 0
4.2 | Supply and weld a 12mm high tensile steel rod along the bases of the posts for anchoring the chainlink to the ground along the whole length of the fence.Allow for excavating 200mm deep along the fence to fix the rod. | LM | 40 |  | 0
4.3 | Allow for curing of all concrete works | Item | 1 |  | 0
4.4 | Supply and fix 3No strands of 12G barbed wire bound onto either sides of the Y post using 3mm galvanised wire as shown in the drawings. | LM | 280 |  | 0
4.5 | Ditto for posts | LM | 240 |  | 0
4.6 | Supply and and fix 2500mm high HEAVY GUAGE chainlink to posts using 3mm galvanised wire. Allow for securing the chainlink to a 12mm reinforcement bar welded at the base btween the posts. | LM | 40 |  | 0
4.7 | Supply and fix razer wire secured on the chainlink, barbed wire and Y posts by binding wire and rolled approximately 600mm dia. | LM | 40 |  | 0
4.8 | Prepare and apply one under coat of epoxy based primer and two finishing epoxy based paints to metal surfaces n.e 250mm in alternate bands of 300mm | No | 16.67 |  | 0
Total of Bill NO. A, BoQs of SOLAR FENCE AND GATE, carried forward to summary |  |  |  |  | 0

## Summary
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURE WORKS- DHAGAX-DHEER, TOG-DHEER- SOMALILAND.
Summary
ITEM | DESCRIPTIONS | Overall Total cost (USD)
1 | Total of Bill NO. A, BoQs of new construction of elevated Water Tank | 0
2 | Total of Bill NO. A, BoQs of Borehole supplies | 0
3 | Total of Bill NO. A, BoQs of distribution Pipiline to communities | 0
4 | Total of Bill NO. A, BoQs of Water Kiosks | 0
5 | Total of Bill NO. A, BoQs of animal trough | 0
7 | Total of Bill NO. A, BoQs of Solar installations | 0
8 | Total of Bill NO. A, BoQs of construction caretaker room | 0
8 | Total of Bill NO. A, BoQs of Solar fence and main gate | 0
Grand Total of Summary- USD $ |  | 0
Important Note: Locations of boreholes to be rehabilitated, Solar systems, and pumping area will be in the following coordinates: Dhagax-dheer Borehole GPS Locations 8.415191, 45.766391
Contact Person:…......................................................................................................................................................
Company Name:…………………...................................................................................................................................
Address: ……………………………………………………………………………………………...................................................................
Tel No: ………………………………………………………………………………………………….................................................................
Date:………………………………………………………………………………………………….......................................................................
Signed:…...............................................................................................................................................................................
Stamp: ...………………………………………………………………………………….................................................................................