## New Wateryard (hidden)
BILL OF QUANTITIES
South Sudan Enhancing Community Resilience and Local Governance Project (ECRP)
Project Description: Wungok Village GPS : N=10.07358889, E=29.89319444 (Wungok Boma)-Werthen Payam, Abouny Village GPS: N=9.939001, E=29.825724 (Wunkur Boma)-Aliiny Payam ; Ayija Village GPS: N=9.88216667, E=29.94313889 (Akotweng Boma)-Nyiel Payam; Drilling and construction of 3 new water yards installed with solar panels and submersible pump;
Name of Bidder:
I | Description | Unit | Quantity required for project | Unit Cost [USD] | Total cost (USD)
BILL NO 1 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT |  |  |  | 0
1 | SOLAR SYSTEM
1.1 | Supply and installtion of a Dayliff or Lorentz solar system providing at least 36m3/day considering 6 hours of sunshine. The system shall comprise of a submersible pump and well probe, float switch, smart PSU with wireless data connect, PV Disconnect, surge protector and lighting arrestor with a minimum of 1 piece of 8‐foot copper‐plated grounding rod. Design of the solar system needs to be inspected and validated by IOM prior to procurement and installation. | LS | 1 |  | 0
2.1 | Supply and install of a parallel series solar pannels certified to ISO, IEC 61215 and 61730 (TÜV Rheinland) and CE oversized by 1.2 to 1.3 times the motor size. The solar panels shall be mounted facing North and a tilt angle of 7deg, mounted onto a fabricated frame above the storage tanks. | LS | 1 |  | 0
3 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT
3.1 | Horizontal installation of 3 flow meters, at the inlet of the storage, and 1 per water kiosk. | pcs | 3 |  | 0
3.2 | Supply and installation of 6.0 metre high metalic stand tower for tank, evenly coated with a layer of anti-oxide paint and overlayed with an additional coating of grey/silver paint and fitted with a hooped cat-ladder, top walkways of 2.1mm thickness and safety hand railings. Tower to comply to manufacturing standards: Dead/Live load analysis to BS 6399. Wind load analysis to CP3 ch V 1972. Structural steel work to BS 5950 Part 1 1990. | LS | 1 |  | 0
3.3 | Supply and installation of 2 PVC high quality water tank of 5,000 liter each (Toptank recommended). | pcs | 2 |  | 0
3.4 | Supply and installation of 2-1/2'' HDPE underground distribution and uPVC, PPR class 10 above ground pipeline and fittings. | m | 300 |  | 0
4 | WATER YARD SITE LAYOUT
4.1 | The borehole shall be fitted with a well head casted in a concrete platform of minimum 0.3m height and protected by a man hole with a cast iron trap fitted with a lockable system. | LS | 1 |  | 0
4.2 | Levelling of the site and laying a 300mm thickness well compacted murram of 60% minimum aggregate approved by the IOM Supervisor prior to installation. | LS | 1 |  | 0
5 | REPORTING
5.1 | Submit well completion report as per IOM template, including results of water quality analysis. | No | 1 |  | 0
BILL SUMMARY
BILL NO 1 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT | Unit | 3 | 0 | 0
|  | GRAND TOTAL |  |  | 0

## Water Yard Rehabilitation (hidden)
BILL OF QUANTITIES
South Sudan Enhancing Community Resilience and Local Governance Project (ECRP)
Project Description: Abon 2 Village GPS: N=9.918025, E=29.98141389 (Waukok Boma)-Pariang Payam, - Drilling and rehabilitation of existing water yard installed with solar panels and submersible pump, Pariang County, Unity State
Name of Bidder:
I | Description | Unit | Quantity | Unit Cost | Total cost
BILL NO. 1 | PRELIMINARIES |  |  |  | 0
Notes:
| All the Bidders are requested to refer "Pricing Preamble and notes below" and works items of this Bills of Quantities shall be priced to fulfill the requirements there-in. Also see that no page or items are missing prior to pricing of this bill of quantities. | Note
| A list of typical general items are given below. However, the Bidder is requested to price only those items that may affect this Contract. | Note
| If no price has been stated against any item hereunder, the Contractor shall not be entitled to claim any money for such items even though he is obliged to execute the work or provide services described therein. Preliminary items priced by the Tenderer are deemed to include the cost of unpriced items. | Note
| Cost and expenses in connection with any other preliminary item which is not listed below, but is necessary for the due completion of works, is deemed to be included in the tender rates. | Note
1.1 | Site Facilities |  |  |  | 0
1.1.1 | Mobilization and demobilization from the site including all requirements of Guideline GHS12 - Site Establishment - Preparation works, protection of existing structures, materials and items, site boundaries, information board, office and welfare facilities, storage sites, generator, site reinstatement, safety, and security | 1 | Lump Sum |  | 0
1.1.2 | Fabricate a metal visibility plate 100 x 80 mm to be wall mounted. Art work of name board will be issued by IOM | 1 | each |  | 0
1.2 | Sites Operations |  |  |  | 0
1.2.1 | Allow for setting out of works in accordance with drawings; liaise with client to establish exact boundaries and other written information given by the Engineer and obtain written approval from the relevant government authorities for setting out, street and building lines before commencements of construction; Checking of any setting out or of any line or level by the Engineer shall not in any way relieve the Contractor of his responsibility for the accuracy thereof. | 1 | Lump Sum |  | 0
1.2.2 | Tools, plant, and scaffolding | 1 | Lump Sum |  | 0
1.2.3 | Allow for providing all necessary safety measures to workmen (provision for proper usage of Personal protective equipment (PPE)). | 1 | Lump Sum |  | 0
1.3 | Insurances, Bonds & Fees |  |  |  | 0
1.3.1 | Allow for Contractor's All Risk Insurance Policy, including third party liability and from the starting date until the defects liability certificate has been issued, the risks of personal injury, death, and loss of or damage to property (including, without limitation, the works, plant, materials, and equipment) which are not employers risk but are contractors risk Allow for insurance against claims for worker's compensation. Engineer's and Consultant's representatives, shall be included in the Insurance Policy. Allow for insurance against loss or damage to the works, adjacent structures, any existing overhead and/or underground services that may cause damages during the construction | 1 | Lump Sum |  | 0
BILL NO. 4 | REHABILITATION OF EXISITING WATER YARD |  |  |  | 0
4.1 | Supply and Installation of solar pump, solar panels and accessories | Unit | Quantity | Unit Rate | 0
4.1.1 | Supply and install Deep Well Submersible Pump, 4" 2 HP, 220V, 35 GPM, 400 ft Max, long life, to provide at least 48m3/day considering 8 hours of sunshine and a total dynamic head of 90m. The system shall comprise of control panel, submersible cable of at least 110m, float switch, UPVC Riser pipes and adaptor set, surge protector and lighting arrestor with a minimum of 1 piece of 8‐foot copper‐plated grounding rod. Design of the solar system needs to be inspected and validated by IOM prior to procurement and installation. | LS | 1 |  | 0
4.1.2 | Supply and install in a parallel series solar pannels 300 W and above, certified to ISO, IEC 61215 and 61730 (TÜV Rheinland) and CE oversized by 1.2 to 1.3 times the motor size. The solar panels shall be mounted facing North and a tilt angle of 7deg, mounted onto a fabricated frame above the storage tanks. | LS | 1 |  | 0
4.2 | Water tank rehabilitation, Water distribution network and rehabilitation of existing water points. |  |  |  | 0
4.2.1 | Horizontal installation of 4 flow meters, at the inlet of the storage, and 1 per water stand tap station | pcs | 4 |  | 0
4.2.2 | Repair and modify the existing 6.6 metre high metalic stand tower, including providing metallic solar panels carrier welded to the existing stand tower at least 1m above water tank, ensuring strong bracings and all necessary support to resist effect of wind force. Ensure that the solar panel carrier is inclined and oriented appropariately. Conduct thorough check on the exisiting 20M3 metallic circular tank against any leakage, evenly coated with a layer of anti-oxide zinc phosphate paint and overlayed with an additional coating of grey/silver paint and fitted with a hooped cat-ladder, top walkways of 2.1mm thickness and safety hand railings. | LS | 1 |  | 0
4.2.3 | Supply and installation of 2-11/2'' HDPE underground distribution and uPVC, PPR class 10 above ground pipeline and fittings. | m | 400 |  | 0
4.2.4 | Rehabilitation of 4 water points with 3 Talbot Talflow self closing taps each in hollow block and concrete masonry including construction of a drainage channel and a soak away pit. | pcs | 4 |  | 0
4.3 | SITE LAYOUT |  |  |  | 0
4.3.1 | The borehole shall be fitted with a pedestal stand casted raised at least 0.7m in a concrete platform of minimum 0.3m thick and protected by a man hole with a cast iron trap fitted with a lockable system. The well must have provision for deep meter hole to check static water level and depth of BH | LS | 1 |  | 0
4.3.2 | Levelling of the site and laying with well compacted murram of 60% minimum aggregate laid at interval not exceeding 100mm thick until 300mm thickness is achieved, as approved by the IOM Supervisor prior to installation. | LS | 1 |  | 0
4.3.3 | Supply and installation of a fence 8m x 8m to secure the solar system and the borehole (if feasible). The fence shall be constructed using Y shaped circular steel hollow section tubes of 50mm diameter by 3mm thickness or casted in a concrete (1:2:4) foundation (W: 0.3 X L: 0.3 X H: 0.7 m). The top part of the pole shall be welded with V-shaped of 500mm length and installed with razor wire of 0.9m diameter. The height of the pole above ground shall be determined by the height of the chain link supplied but should be of minimum 1.9m. The poles shall be installed 1.5 meters apart and reinforced using 3 lines of tension wire. An apron of 200mm wide shall be casted all round along the fence perimeter | LS | 1 |  | 0
4.3.4 | Installation of a gate frame constructed with 2 pieces of 100mm x 100mm x 3mm (4x4 inch) hollow section frame, each supported by an additional member placed at 60deg angle from the vertical pole. The gate itself shall be constructed with 60mm x 60mm x 3mm hollow sections shutter frame and covered with wire mesh. | LS | 1 |  | 0
4.3.5 | Fence and gate shall be evenly painted with a single layer of anti-oxyde paint and overlayed with an additional coating of grey/silver paint. | LS | 1 |  | 0
4.3.6 | Supply and installation of 2 modular all-in-one solar street lights, attached directly onto the solar frames and secured by razor wire. | pcs | 2 |  | 0
BILL SUMMARY
BILL NO. 4 | REHABILITATION OF EXISITING WATER YARD | Unit | 1 | 0 | 0
|  | GRAND TOTAL |  |  | 0

## Bill No. A-MILK
BoQs FOR SOLAR POWERED MILK COOLING FRIDGE AND MILK CONTAINER 20 LITTER CAPACITY , MSME.
| BoQs of MILK PROCESSING [SOLARIZATION MILK] Solar powered milk cooling fridge for small holder women milk street vendors In Somaliland. |  |  |  | Ref:PRN:
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | BoQs of Supply and Installation of ] (BoQs for Solar powered milk cooling for Enhance the availability of both on-grid and off-grid renewable energy solutions for households and Micro, Small, and Medium Enterprises (MSMEs )
A 1 | BoQs of Supply and Installation of ] (BoQs for Solar powered milk cooling system in Somaliland
1.1 | • Temperature: 15~ -18℃ • Refrigerant: R134a • Capacity:-358L -450L • Color: Silver • Style: Chest Deep • Power Source: Solar DC battery, Battery, Solar • Input voltage: 12V 24V • Solar panel: Class A Mono • Door: Single Folding • Temperature Type: Single-Temperature • After-sales Service Provided: Free spare parts • Warranty: 5 years • Operating Language: English • Application: Outdoor, garage, Commercial, Household, Hotel • App-Controlled: NO • Private Mold: Yes • Logo/Pattern: Silk screen printing • Brand Name: Quality motivated • Model Number: 2024 and after • Application: Commercial outdoor (street milk business) • Climate type: Arid and semi-arid lands (ASAL). Resilient to hot weather like the one for Somalia, shockproof and durable for handling in rough road. • Digital display with individual temperature control: LED display touch control panel makes temperature adjustment easy (if possible). • Free spare parts accompanied: Welcomed • Conformity with German/EU Standards ( CE) | Unit | 22 |  | 0
1.2 | •Solar Cell: Monocrystalline • Surface material: ETFE • Cloth color: Black • Open size: 2510 × 1100mm • Net weight 8.4 KG • Type of Connector: XT60 + Anderson + GX16 + DC • Additional design: Kickstands • Certifications: CE, FCC, ROHS, REACH • Conformity with German/ European Standards (CE ) • Standard Test Condtion: Irrandiance 1000W/㎡ • Module temperature: 25℃,AM=1.5 • Maximum power(Pm): 450W • Voltage at max power(Vmp): 18V • Current at max power(Imp): 22.2A • Open circuit voltage(Voc): 21.6V • Short circuit current(Isc): 24.2A • Temperature Coefficient of Pmax: (-0.41% /ºC) • Temperature Coefficient of Voc: (-0.33% /ºC) • Temperature Coefficient of Isc: (+0.06% /ºC) • Power Tolerance: -0%, +5% • Maximum System Voltage: 1500V DC • Maximum Series Fuse Rating: 25A • Operating Temperature: -20℃~65℃ • Noct*: 45℃ ± 2℃ • Warranty: 5 years product warranty on materials and workmanship • Power is not less than 95% in 5 years. Battery Type Deep Cycle Sealed Lead Acid (Gel or AGM) Nominal Voltage 12V DC Capacity 150Ah (can vary between 100Ah–200Ah based on load and autonomy) Energy Storage 1.8 kWh (12V × 150Ah) Design Life 5–8 years (depending on usage and ambient temperature) Charge Efficiency ≥ 95% Discharge Depth Up to 80% DoD (Depth of Discharge) Operating Temperature -10°C to +50°C Cycle Life 1000+ cycles at 50% Depth of Discharge Dimensions (L×W×H) ~ 483 × 170 × 240 mm (varies slightly by manufacturer) Weight ~ 40–45 kg (for 150Ah) Terminal Type M8 or F12 (depends on model) Certifications ISO 9001, CE, RoHS. This including all the necessary fittings and installation of the solar system` | Unit | 20 |  | 0
1.3 | Inverters – 15KW: (Model M5000h-48BP PV Off-Grid Inverter) Supply, install, connect and operate DC/AC offgrid tie 3-phase inverter with data communication and energy meter with followingspecification: Inverter Mode - Battery Input: 48VDC, 117A - Type of Battery: Lead Acid/ Lithium - Rated Power: 5000VA/5000W - AC Output: 230VAC,50/60Hz, 40A, 1dim - AC Input: 230VAC,50/60Hz, 40A, 1dim - Max AC charge Current 80Amp - Max. PV Input Voltage (VOC): 450VDC - Max. PV Input Current 18A - MPPT Volatage Range: 120, 430VDC - Max. Charge Current 100A - Coomunication: WIFI/GPSRS (Option) The inverterwith must be suited to any PV module configuration, and depending on the system design and installation proposedand for the future extended also. (Model M5000h-48BP PV Off-Grid Inverter). The DC max power input rating should be equal ormore than 15KW of the PV modules capacity at standard test condition. The inverter unit shall be suitable with weather conditionas indoor installations. The inverters AC nominal power output rating must be equal or greater than 5KW to be total of 15KWp compatible with the AC loads design. The inverter must include the safety concepts such as (triple protection with optiprotect, electronic strings fuses, self-learning string failure detection, DC surge arrestor type 2 ) to ensure max availability. The price includes : • Supply, install and connect (monitoring and controlling unit) for all PV solar system installed especially compatible with the inverters, with all needed accessories, interface modules & data cables and all connections needed to complete and connect the monitoring system to internet. | Unit | 3 |  | 0
1.4 | Battery Bank: Supply, install, connect and operate Lithium Ion Battery capacity of 240kWh with following specifications: - Normal volt (V): GBP480 - Normal capacity: (AH) 100 - Working volt range: 42-56.25 - Recommend charging volt (V): 52.5 - Recommending discharging cutoff volt (V): 45 - Standard charging current (A): 50 - Max. Discharging current (A): 100 - Protection: IP20 - Max Dimension (W*D*H) for rack typr: 482.6*535*175 - Net Weight: 56kg The batteries must provide high-quality and achieving superior performance, the manufacturing date must be new and not morethan 6 months, suitable for every type of applications especially for solar renewable energy, designed Service Life 10 years with low internal resistance, designed to be deeply discharged. The Battery should provide benefits of being maintenance free, caseflame retardant & non-hazardous. The price Includes supply, install & connect Battery temp. sensor (BTS) and the following: • All necessary DC cables between the batteries together and to the battery fuse box to have a complete operational circuit withall bus bars, conduits, clamps, stainless steel bolts, washers and cable end terminations and all needed materials to complete thejob. All DC cables must be sized in accordance with the installation requirements applicable on site ,the allowable voltage drop must be less than 1%. • Battery Banks rack from the same manufacturer of the batteries with dividers and all needed accessories to finish the job. the rack must be enough to carry all the weight of the required batteries for the system. • The contractor mustsubmit manufacturer warranty for each battery cell for a period 10 years. All works and | Unit | 5 |  | 0
1.5 | Battery Rack : (Wall Mounting) Batteries shall be installed in clean, dry locations. They must be secured against falling items and dirt, The battery racks will be built in parallel connected racks using the battery distribution panel that's according to mounting circuit diagram.The battery is designed and built in conformity with the latest technical rules at the time of its development and production, so it is safe to operate. Danger maybe presented by the battery, if it will is used for other than the intended purpose and by unskilled personnel.All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | Unit | 4 |  | 0
1.6 | CABLES AND ACCESSORIES DC cables 8mm x 500m, surge protectors, Combination boxes, MCB, Fuses, MC4 Connectors core cable from luminay to battery. 2 core cable from Panel to battery. nominal cross sectional area of conductor 50sq mm wire for battery connections. Assorted nuts and bolts for panel fixing. Lugs for wires. Battery rack from metal , Allow for all necessary AC wiring connectionsof 10mm x 1,500 meter from the power source (Solar) to the All workstations including fixing, distribution boards, sockets and trucking pipes, AC circuit breakers for each MIDAS Station, as directed on the site specifications and supervisor instructions approval. | Set | 1 |  | 0
1.7 | Construction of Storage Room (3x4m) Supply and construct 3x4m Room to store batteries and solar inverters, Room shall be equiped with one A/C 9000BTU, Room shall have two windows and a door, floorbed should be suitable to withstand batteries wieght and shall have tiles. All works andmaterials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | LS | 1 |  | 0
1.8 | Use for milk transportation and storage. • Capacity: 20 L. •Material Grade: Food Grade type 304 Stainless Steel. The material should have high corrosion resistance. • Should have a secured stainless steel food grade lid that should close the can tightly for safe transportation, with latch. The lid should be airtight and leak-proof to prevent contamination and maintain freshness. • Should have firmly installed, well-fitted riveted double sided wire handles for easy transportation. | Unit | 40 |  | 0
1.9 | PV Mounting structure: Supply and install Module mounting structure from Galvanized Steel structures to fix the photovoltaic panels. The structure must be suitable to the dimension of selected PV modules and PV numbers, the mounting provides a fixed inclination of the modules 30 degree with vertical supports, plates, the structure profile includes bracing and double hot galvanized angles for dividers.Themounting structures and the foundations must be designed structurally to be suitable to withstand all static loads (weight of modules, wind loads etc) that might occur according to the Site conditions. The mounting structure components are bonded together to guaranty potential equalization. All works and materials must be according to drawings, specifications and supervisor instructions and approval. | LS | 1 |  | 0
1.1 | Fabrication, supply, and installation of complete street vending kiosk unit – Dimensions approximately 1.5m (L) × 1.20m (W) × 2.2m (H); fabricated using 25mm × 25mm mild steel square tubes, primed and painted with anti-rust enamel paint. Includes the following integrated components: • Roofing canopy made of 1mm thick galvanized steel sheet, powder-coated or painted blue and white.• Working counter top (1.5mm thick mild steel sheet) welded and reinforced.• Two lockable lower storage compartments with sheet metal doors, hinges, handles, and padlock hasps.• Branding and labeling with project logo and identification number | Unit | 20 |  | 0
1.2 | Installation, testing and Commissioning | LS | 1 |  | 0
1.3 | Transport and logistics | LS | 1 |  | 0
B.1 | Attached for Images is used for just visualising the requirement.
Total of Bill NO. A, BoQs of SOLAR POWERED MILK COOLING FRIDGE AND MILK CONTAINER 20 LITTER CAPACITY, carried forward to summary |  |  |  |  | 0

## Summary
BoQs FOR SOLAR POWERED MILK COOLING FRIDGE AND MILK CONTAINER 20 LITTER CAPACITY , MSME.
Summary Ref:PRN
ITEM | DESCRIPTIONS | Unit | Quantity required | Total cost for Bill NO. | Overall Total cost (USD)
1 | Total of Bill NO. BoQs of SOLAR POWERED MILK COOLING FRIDGE, SOLAR CELL AND MILK CONTAINER 20L All REUIRED DETAILES | Milk cooling Fridge | 1 | 0 | 0
Grand Total of Summary- USD $ |  |  |  |  | 0
Important Note:
Contact Person:…......................................................................................................................................................
Company Name:…………………...................................................................................................................................
Address: ……………………………………………………………………………………………..................................
Tel No: …………………………………………………………………………………………………..............................
Date:…………………………………………………………………………………………………....................................
Signed:…...............................................................................................................................
Stamp: ...………………………………………………………………………………….......................