## BoQ - Blank
SUPPLY, DELIVERY, AND INSTALLATION OF FOUR (4) SOLAR-POWERED SYSTEMS COMPRISING A 22.61 kWp SOLAR PV SYSTEM INTEGRATED WITH 11 kW SURFACE PUMP FOR IRRIGATION TO SUPPORT FOUR SMALLHOLDER COOPERATIVE FARMS IN IN JOWHAR/BAAREY, HIRSHABELLE STATE OF SOMALIA
Item # | Description/ Specifications | Unit(s) | Quantity Required | Unit Price (USD) | Total Price (USD)
1 | Supply and installation of 11kW 3-phase centrifugal AC pump (complete with motor AC drive and the pump end) with a flow rate of 125-140 cubic meters per hour and a head of 15-25 meters. The pump should have a frequency range of 30-50Hz with good efficiency. The pump should be from reputable and known brands such as Lorentz, Grudnfos etc with a minimum warranty of 2 years. | Pc | 1 |  | 0
2 | Supply and installation of high efficiency 15kW solar pump Controller, with hybrid power function to mix solar with other available power. It should have Maximum Power Point Tracking (MPPT), multiple analog and digital sensor such as sunesor and water sensor to prevent the pump from dry running. The controller should be from reputable and known brands such as Lorentz, Grudnfos etc with a minimum warranty of 2 years. | Pcs | 1 |  | 0
3 | Supply and installation of High-efficiency Solar PV Modules, preferably LONGI/Jinko/JA solar,Capacity:595W or above,type: Mono, Warranty 20 years for total system capacity of 22.61 kWp | Watt | 22610 |  | 0
4 | Supply and Installation of Alluminium mounting structure with lower height to be not less than 1M. The structure should have all clamps such as end clamps, middle clamps and rail clamps. The work should be inclusive of the concrete foundation with minimum height of 500mm (200mm below the ground), length 400mm and width 400mm. | PCS | 22610 |  | 0
5 | Supply and Installation of 100mm HDPE Sunction pipe (the diamter of pipe must be equal to the diameter of the outlet of the pump)with sunction pipe from the river to the pump | M | 20 |  | 0
6 | Supply and Installation of 100mm HDPE Discharge pipe (the diamter of pipe must be equal to the diameter of the outlet of the pump) from the pump to the water canals with associated fittings such as non-return valve (shaboole), flanges etc. | M | 50 |  | 0
7 | Supply and Construction of reinforced concrete foundation block for surface pump installation dimensions (L:1.2m x W: 1.2m ) H: 1.5m-0.7m depth below the ground, including excavation gravel bedding, blinding, reinforced concrete (C25), steel reinforcement (Y12 bars), formwork, embedded stainless steel anchor bolts (M16), drainage piping, and all skilled and unskilled labor necessary for complete execution as per specifications near riverbank location. Two foundations, one for high water levels and the other for low—so the pump always stays near the suction point | Lsm | 2 |  | 0
8 | Supply and fabrication of enclosure for the controller, PV disconnect and other accessories. The enclosure will be placed near the PV mounting area, and should have lockable 2 doors. The bidder to consider the sizes of the proposed electronic devices. | Lsm | 1 |  | 0
9 | Foot Valve of same dimensions as pipe to be connected to end of the suction pipe to prevent backflow and maintain prime | Unit | 1 |  | 0
10 | Flanges to connect to inlet and outlet of the surface pump and to the sunction and discharge pipes respectively. | Unit(s) | 2 |  | 0
11 | 1x6 mm2 flexible cable (PV CABLE) (black and Red) | M | 150 |  | 0
12 | 4x16 mm² 4 core flexible cable (PUMP CABLE). It should not have joins except at the connection point of the pump. | M | 50 |  | 0
13 | PV Disconnect 1000-40-5 | Pc | 1 |  | 0
14 | PV Protect 1000-125-4 | Pc | 1 |  | 0
15 | Manual Changeover Switch 200A | Pc | 1 |  | 0
16 | Installation sundries such as grounding rods, conduits, pvc pipes, white board for mounting the controller, etc. | Lsm | 1 |  | 0
17 | Installation charges including the training of at least 2 local operators from the begin of the installation works to the testing of the system. | Pcs | 1 |  | 0
Total Cost for ONE 22.61 kWp solar PV system and Irrigation Pump of 11kW |  |  |  |  | 0
Total Farms - 4 Farms |  |  |  |  | 4
GRAND TOTAL FOR 4 SIMILAR SYSTEMS |  |  |  |  | 0