## BOQ- water System-dhabar-dalol.
BOQ FOR MINI- WATER SUPPLY MINISYSTEM IN DHABARDALOOL.
1) Bill of quantity of drilling well
No | DESCRIPTION | UNIT | QTY | RATE($) | Total
Drilling well.
1 | Excavation and Earth works .
2 | Mobilization: materials and labour mobolization, Visibility study, stake holders meeting and transportation cost. | LS | 1 |  | 0
3 | Clearance: Clean bushes, debris, heavy Stalwarts and small mould away from the shallow well site 7m in every direction of the shallow well. | LS | 1 |  | 0
4 | Excavation Works: Digging well pit shafts to enough depth to reach underground water, this work includes take away the excated rocks, sand and other materials away from the shallow well 7m in every direction. | M3 | 85 |  | 0
5 | Extra -excavation works allowance: digging heavy bed rocks on the bottom of the shallow well in 8% of the exavation. | M3 | 5.652 |  | 0
6 | Sub-Total of exavation and clearance works |  |  |  | 0
7 | Concrete rings and back filling
8 | Dewatering: dewatering fuel for water pump during well excavation. | Hrs | 32 |  | 0
9 | Concrete works: In-situ Concrete works casted according to instructions of TAAKULO WASH engineer. | cum | 15 |  | 0
10 | Embed U-shaped with 12mm steel bars ( 40cm ) into rcc ring concrete to allow anchorage as instructed by the TASCO WASH engineer. | NO | 3 |  | 0
11 | Apply two coats of cement plastering on the ring wall smoothly, mix ratio 1:2, both internal and external top ring as instructed by the TASCO WASH engineer. | M2 | 4 |  | 0
12 | Put stone at the back of the porrous bottom rings about first 5 bottom rings and other above 5 rings will back fill and compacting with selecting material of clay silt, | M3 | 23.55 |  | 0
13 | Sub-Total for concrete rings and back filling |  |  |  | 0
14 | Well apron and drainage gully
15 | 50mm thick concrete mix of 1:2:4 blinding over aproved hard-core beds to level under the apron. | M3 | 0.8 |  | 0
16 | 120mm thick RCC concrete mix 1:2:4 concrete slab manually compacted over the blinding bed to levels under apron (12mm thickess steel bars for each side.) | M3 | 0.75 |  | 0
17 | lay a 50mm thick screed with awood float followed with acement/water niro with a steel float smooth finish on concrete floor | M3 | 0.314 |  | 0
19 | Instal and provide metal manhole conver of 700mmx700mm with 50x50mm Angle frame. | Ls | 1 |  | 0
| SUB-TOTAL COST FOR Well apron and drainage gully |  |  |  | 0
| Grand Total for one water well. |  |  |  | 0
2) BOQ for Construction of Elevated water tank, solar power and pipe line water extension.
Construction of RCC Circular Elevated tank of 15Cum (3m dia*2.2m) which is 4 meter above ground.
1 | Clearing of site from debris, rubbish etc (7x5)m | m2 | 35 |  | 0
2 | Excavation of column footing (1.8x1.8x1.5)m, 4in numbers | m3 | 19.44 |  | 0
3 | Casting of Column footing(1.6x1.6x0.5)m Y14 at 200mm spacing, 4 in numbers | m3 | 3 |  | 0
4 | Casting of 4 columns from footing up to base slab(0.4x0.4x5)m @ 4 columns with RC concrete mix ratio 1:2:4. 6Y14? R8 stirrups. At 200mm c/c | m3 | 4.5 |  | 0
5 | 40cm thick Rubble stone foundation 30cm above the ground level and 20cm below ground level | m3 | 2.4 |  | 0
6 | Backflining,leveling and flooring up to surface ring beam(4x2x)m | m3 | 2 |  | 0
7 | 10cm thick Mass concrete slab on top of the back filled area | m3 | 2.4 |  | 0
8 | Casting of three ring beams, at plinth level, middle and at roof level, (0.4x0.4x0.4),Y12, R8 stirrups,Top primary beams(0.4x0.4)cm with RC concrete mix ratio of 1:2:4. 4Y14, R6 stirrups,Two cross secondary beams at top(0.4x0.4)cm 4Y14, R6 stirrups, | m3 | 3.8 |  | 0
9 | Casting of slab, base slab with RC concrete mix ratio of 1:2:4. base slab,Y12 at 200mm spacing.Y10 on roof slab at . This including the cover slab with the diferent dimension | m3 | 5.9 |  | 0
10 | Casting of tank walls(12Mx2.2x0.2)m with concrete mix ratio of RCC 1:2:4. | m3 | 5.6 |  | 0
11 | Manhole lid 0.6mx0.6m | PC | 1 |  | 0
12 | Outlet GI pipe with valves 2inch with length 0.6m , Over flow pipe 2 inch as well as pressure pipe complete with all the fitting | Lm | 6 |  | 0
13 | Inlet and out let GI pipes Class B with 2 inch diameter including all fitting (straight connector) ascending and decending | PC | 4 |  | 0
14 | 1.5 inch Gl pipe lander fixing outer side of the tank complete with strait sockets and welding pipe for the purpose of lander. | m | 18 |  | 0
| Apply two coats 12mm plastering on the internal and external surfaces of the tank, columns ,Slab bottom surface, cover slab upper surface and beams | m2 | 260 |  | 0
15 | Two coats of White washing on the external surfaces of tank, beams and columns. | m2 | 260 |  | 0
16 | Painting visibility logos on the top of tank walls, as per recommendations of site engineer, to ensure visibility | Lumpsum | 1 |  | 0
17 | Sub Total Cost- Construction of Elevated tank |  |  |  | 0
3) BOQ of Solar system installation and Pipeline , water pump for Dhabardalool villages.
S/N | Description | Qty | Unit | Unite Cost ($) | Total Cost ($)
1 | Supply and installing 8 pcs 560W with model Dusol made in UAE | 8 | NO |  | 0
2 | Supply and install solar mounting frame. all the frame will welded together and the vertival uphold frame will be make of GI pipe 2" galvanized and the upper solar panel frame will be Gi angle 5mm riveted thick with nuts and polts together with solar panel to tighten firnly. The mounting shoul be tilted in angle 15 degree towards direction of sun, and the offset elevation from ground will be 1 meter in lower side. the mounting GI coloumns will placed in a concrete footing box ( 40*40cm) and will be below ground level through excavations of square trench footing (50*50cm). | 8 | pcs (frame per pannel) |  | 0
3 | Provision, Installation, and testing of 1 Pc of Grundfos Submersible solar Pump Power rating (1.4 Kwts) including automatic water level sensor. | 1 | NO |  | 0
4 | 401-1-PV disconnect switch 32A/2pol 1000V/1200V | 1 | NO |  | 0
5 | Supply and install water pump electric cable 6mm sqr, 3 core made in saudi, from water pump to the invertor board. | 70 | NO |  | 0
6 | Supply and install 6 mm2 twin solar Wire (Array to Junction Box and from Junction Box to the switch box). (all wires should be passed through conduits and using rings in its terminals) | 30 | NO |  | 0
7 | acceseries including spilit joint,bolsts and strip tie cable fix wire DC conection | 1 | lumsum |  | 0
8 | Flow control: Supply and fix Original England Pegler 2" none return valve atthe shallow well's 2" G.I. pipe outlet. | 1 | NO |  | 0
9 | Supply materials and install fence with a lockable steel gate for the solar panels compound: Chain link fence, 2-meter- long steel angle bars-15 pcs(poles), Portland cement-5 bags, sand 8 tones, lockable steel gate-1, nails 3”-5Kg,2”- 5kg, locks | 40 | L.M |  | 0
10 | Installation and Transportation Cost. | 1 | lumsum |  | 0
| Subtotal of Solar supply and instalation |  |  |  | 0
4) BOQ for Pipeline installation- 700m water distribution piplines and Construction of communal water kiosk.
s/n | Description of works | Unit | QTY | Unit Cost | Total Cost
A) Installation of water pipeline distribution system.
1 | Excavation and backfilling of pipe trenches, dimensions of the trenches are: width: 40 cm, Depth: 50 cm and length: 700m. | M3 | 140 |  | 0
2 | Supply and installation of 2" HDPE pipe, PN10 from dam water tank, distance of 400m (Include pipe accessories, fittings, sockets, gate-valves, air-valves, tee sections etc), | meter | 400 |  | 0
3 | Supply and installation of 1.5" HDPE pipe, PN10 distribution pipes, from water tank to kiosk and animal troughs, distance of 300m (Include pipe accessories, fittings, sockets, gate-valves, air-valves, tee sections etc), | meter | 300 |  | 0
4 | purchase and installation of 2 inch GI pipes for intlet and outlet. | pcs | 2 |  | 0
5 | Purchase and install all the necessary pipe and GI fittings: GI unions, GI nipples , valve boxes, 2 inch Tees, stop cacks, gate valves and non return volve of 2 inch water meters, GI-HDPE adaptors. | LS | 1 |  | 0
6 | Transportation and installation cost . | 1 | Job |  | 0
| Sub-Total for pipe installation |  |  |  | 0
5) Construction of 2 Water points (kiosks).
1 | Excavation of base foundation trench (2.4x2.8x0.3m deep) | Cu.m | 2 |  | 0
2 | Supplying and laying 250 mm approved hardcore filling spread well rammed and compacted | Cu.m | 1.7 |  | 0
3 | Supplying and laying 50 mm approved lean concrete above the hardcore, spread well and smoothed. | Cu.m | 0.36 |  | 0
4 | Construct a rubble massonary wall of 1.2m*1.6m and 0.55m high, with mortar mix ratio 1:4. | Cu.m | 1.1 |  | 0
5 | Casting 10cm thick RCC top cap above the massonary cubicle foundation with mix ration 1:2:4, and Y 12@20cm c/c for both ways. (1.2*1.6*0.1m) | Cu.m | 0.2 |  | 0
6 | Casting of Vertical RCC wall above the base water point with dimension (1.6m widht*0.7m high* 0.2m thick), mixing ration 1:2:4, Y12mm@20cm c/c with 6mm stirups. | Cu.m | 0.22 |  | 0
7 | Plumping work, including fixing Gi pipe 1", 6 peeckoks, elbows, Gi tee and gate valve. | job | 1 |  | 0
8 | Excavate Soak away pit located 4meters from the structure. The drainage channel to be linked with soak away pit with a 2" PVC drainage pipe. The Soak pit to have 1m Diameter and 1.5metres deep, filled with Hardcore. | job | 1 |  | 0
| Sub-Total one kiosk |  |  |  | 0
| Cost of 2 water kiosks |  | 2 | 0 | 0
6) Construction of Goat and Camel water troughs.
# | Description | Unit | Qty | Rate | Total
1 | Earthwork in excavation for the hardcore fill & for the foundation wall 50cm wide to a reduced level not exceeding 50cm from the natural ground level. This also includes clearing the site from any objectionable material. | m3 | 12.81 |  | 0
2 | Supply and construct 45cm thick random rubble stone foundation wall 1:3. | m3 | 6.25 |  | 0
3 | Supply and backfill with 20cm thick hardcore using good hard stone, well compacted and graded to contain sufficient small pieces to fill all voids. | m3 | 6.56 |  | 0
4 | Supply and cast 5 cm thick blinding layer of 1:3:6 on top of the hardcore layer | m3 | 1.64 |  | 0
5 | Supply and cast reinforced cement concrete slab of 15cm thick with cement concrete 1:2:4 (1 cement : 2 clean coarse sand : 4 stone aggregate of 25mm down), reinforced with 10mm diameter mesh @ 15cm c/c including centering and shuttering complete. | M3 | 4.92 |  | 0
6 | Supply and cast reinforced cement concrete side beams as per the attached drawings with cement concrete of 1:2:4 (1 cement : 2 clean coarse sand : 4 stone aggregate of 25mm down), reinforced with 6 Y12mm rebar and R6mm stirrups @20cm c/c. | M3 | 1.05 |  | 0
7 | Apply two coats of cement sand plastering, 1:3 on internal and external surfaces of the partition wall and side beams. This also includes a cement sand waterproof floor screed. | M2 | 8.4 |  | 0
8 | Apply two coats of white wash followed by two coats of distempering on exterior surfaces | M2 | 4.2 |  | 0
9 | Supply and fix 2-inch GI inlet pipe and gate valve complete with all necessary fittings, inside the control chamber, refer the attached drawings. Rate shall also include the provision and installation of lockable steel cover for the control chamber as per the attached drawing and instructed by the engineer. | Pcs | 2 |  | 0
10 | Supply 1 pilboard with visibilty, as well Painting visibility logos and text on the top of tank walls, kiosks, animal troughs, water well as per recommendations of site engineer, | lump | 1 |  | 0
Sub-Total one trough. |  |  |  |  | 0
| Grand total of two Animal trough, Camel + shoat troughs |  |  | 2 | 0
Grand Total - Mini-water supply system in Dhabardalool |  |  |  |  | 0