## Water extension
World Vision International
BOQ of water pipelie extension in Odweyne town, Odweyne district
Note: All Unit rates should be included a 3% Sales tax for each line item.
No | Description of Activities. | Unit | Qty | U.Price $ | Total cost $
1 | Earthwork, Water Connection, Sumbersible and Accessories.
1.1 | Excavation, backfilling and compacting of pipeline trenches with a depth of 60cm, 40cm wide from Odweine Haffir dam to the elevated tank to a distance of 2225m, and from Elevated tank in the town to the Main pipe going to the town with a distance of 246m, 60cm deep and 40cm wide. | m3 | 593.04
1.2 | Supply and install PN16, 2.5 inch HDPE plastic pipe from earth dam to the existing elevated tank in Odwiene town with a distance of 2225m.This should includes all necessary fittings, accessories, tools and testing. | m | 2225
1.3 | Supply and install PN10, 3 inch HDPE pipe of 246m for the outlet pipe from elevated tank to the main existing water connection . This should includes all necessary fittings, accessories, tools and testing. | m | 246
Sub-total |  |  |  |  | 0
2 | Elevated tank Fencing Rehabilitation
2.1 | Supply and fix Galvanized chain link wire mesh (2m height and 25m length and 5mm thickness) while removing all existing and damaged fence parts. | Rolls | 1
2.2 | Supply and Install angular bars of 16 pcs, spaced at 1.5m, each should be 50mmx50mmx4mm, and 3m heigh, each should have 3 fabricated holes fot holding metal posts. | Pcs | 16
2.3 | Prepare and cast a plain concrete around a chainlink fence, the concrete should be 0.15m wide, 0,15 deep and 25m long. Use 1:2:4 mix ratio for concrete and install a good formwork. | m3 | 0.5625
2.4 | Provide and fix 2 rolls of binding wire each 5kg on top of Chainlink fence. | Rolls | 2
2.5 | Supply and Install Lockable single gate with 2 inch MS Pipe Frame, 1m wide 2m height with concrete footings. | Pcs | 1
2.6 | Supply and fix Barbed wire of 25Kg, zinc galvanized steel, 25m length, 2mm thick. | m | 25
Sub-total |  |  |  |  | 0
3 | Solar pumping installation
3.1 | Provide, test and Install of 1 grundfos sumbesible pump; SP 11-27, 1 x 98900422, Rated with 11.7 m³/h, 62.1m head and Power of 5.5Kw, or an alternative approved pump including a power cable with a miniumum lenght of 80m, 6mm2 and with all accessories as per attached document in the Main Haffir dam, and secure it with a Concrete box as per word vision engineer's guidance. In case of an alternative pump, provide the data sheet and the ISO certification | Pcs | 1
3.2 | Supply, Test and Fix a Grundfos controller; RSI 3x208-240V IP66 7.5kW 31A and connect with a Pump. | Pcs | 1
3.3 | Solar module: 14 x NN 350W; 9 ° tilted OR EQUIVALENT, Monocrystalline or equivalent . Provide data sheets for any alternative offered. Note that the Solar panels will be installed in together with existing panels on site | Pcs | 14
3.4 | Well prob sensor | Unit | 1
3.5 | PV Disconnect 1000-40-5 | Unit | 1
3.6 | Cable16 mm² 3-phase cable for power | m | 80
3.7 | Framed Solar Mounting structural steelwork; complete with and including all welded and bolted connections; and including one shop coat red oxide, zinc chromate, or similar and approved primer and 2 finishing coats of gloss oil paint after erection as Shown in the design and as directed by the Engineer. The tower to be 3m high on the lowest end. The tower to be encased in of 400x400x1000mm reinforced concrete base pads | LS | 1
3.8 | Any other solar accessories and solar packages including wiring assessories for the solar panels and any other that may have not been explicitly covered in this BOQ. Including U/G Cables,Earthing etc | LS | 1
3.9 | Supply, test and install OVR PV 40-1000 P, Surge Protection. | Pcs | 1
SubTotal for elevated tank fencing |  |  |  |  | 0
0
| Total cost of pipeline extention |  |  |  | 0

## Summary sheet
Summary of Odweyne village water extension
Item | Description | Amount ($)
1 | Odweyne Water extension | 0
Grand Total cost |  | 0