## Beer-dhagatuur BH WSS_TenderDoc
Tender Documents _ Rehabilitation of the Beer-Dhagaxtuur BH WSS - Ancillary Works
No | Description | Unit | Quantity | Unit Price | Total Price
A | CONSTRUCTION OF 50 M3 CAPACITY AND 10M HIGH ELEVATED RCC RECTANGLE WATER RESERVOIR
1 | Construct 50cum capacity and 10m high elevated RCC rectangle water reservoir. In detail, please see the drawing
1.1 | Site clearance and ground leveling | Sqm | 60
1.2 | Excavation of foundation trenches of 0.5m wide and 0.70m depth | Cum | 8
1.3 | Pits for Column footings for 140x140cmx120cm (6 Nos) | Cum | 13.4
1.4 | Lay on the bottom of foundation pits, 10cm thick lean concrete of class 15 (1:3:6) ratio of cement-sand-gravel blinding of 5cm thick. | Cum | 6
1.5 | Constructing stone masonry foundation wall of 0.4m thick and 0.90m depth | Cum | 10
1.6 | RCC work for column footing 6No. (120x120x30) cm:- Concrete of Class 20 (1:2:4) ratio cement / sand / gravel and as per reinforcement high yield deformed steel, 10 pcs of 16mm steel bars c/c 12cm on the lean concrete putting on perpendicular 10 pcs of 16mm steel bars c/c 12cm. include the rate all carpenter wood work, centering and shuttering completely. | Cum | 2.7
1.7 | RCC ground beam (30x40) cm with cement concrete of class 20 (1:2:4) ratio of cement:sand:gravel, as per reinforcement 6 pcs of Y14mm dia. steel bars and 8mm stirrups @20cm c/c, include the rate carpentry woodwork, centering and shuttering completely. | Cum | 3.7
1.8 | Backfilling and 20cm hard core layer for the bottom floor. | Cum | 8
1.9 | 10cm thick lean concrete of Class15 of 1:3:6 ratio cement:sand:gravel. | Cum | 2
1.1 | RCC work for 6 Nos. columns of 30cmx40cm and 1100 cm high with Class 20 concrete of 1:2:4 ratio (cement:sand:gravel) and including high yield deformed steel, 6 Nos. of 16mm dia. vertical bar and 8mm dia stirrup 20cm c/c and include the rate woodwork, centering and shuttering completely. | Cum | 7.8
1.11 | RCC work in two ring beams of 30cmx40cm (one in the middle and the other below the slab of the tank) with class 20 concrete of 1:2:4 ratio, including high yield deformed 6 numbers 16mm dia. steel bars as principle reinforcement 2 of them at top and 4 pieces at down, 2 of them to be bended as per the direction of engineer and 8mm dia. stirrups @ 20cm c/c include the rate wood work, centering and c/w shuttering. | Cum | 7
1.12 | Constructing 20cm thick RCC bottom slab of the tank with Class 25 concrete of 1:1.5:3 ratio of cement/sand/gravel and Dia.12 iron bars as per principal reinforcement 15cm c/c and as per as per secondary bars 10mm dia @ c/c 15cm. The rate shall include all centering, carpenter work and c/w shuttering. | Cum | 7
1.13 | Constructing 20cm thick and 170cm high RCC walls of the tank with Class 25 concrete of 1:1.5:3 ratio of cement/sand/gravel and Dia.12 iron bars as vertical bars 15cm c/c and as per horizontal bars 10mm dia. @ c/c 15cm. The rate shall include all centering, carpenter work and shuttering complete. | Cum | 9.546
1.14 | Constructing 15cm thick RCC cover slab of the tank with Class 20 concrete of 1:2:4 ratio of cement:sand: gravel and Dia.12 iron bars as per principal reinforcement 20cm c/c and as per as per secondary bars 10mm dia. @ c/c 20cm. The rate shall include all centering, carpenter work and c/s shuttering. | Cum | 5.61
1.15 | Plastering on external sides of the walls, columns & beams with cement sand mortar (1:3). | Sqm | 180
1.16 | Plastering on internal sides of the walls of the tank and the floor slab of the tank with cement sand mortar (1:2) and cement screed as per finishing. | Sqm | 84
1.17 | Whitewashing– Apply three coats with smoothing on all sides of walls. | Sqm | 218.4
1.18 | Distempering– Apply emulsion paint on all sides of outer walls as per finishing until perfect and uniform coverage is reached. | Sqm | 218.4
1.19 | Provide 1 water let-in, 1 water let-out overflow at the top and 2 water let-out at the bottom of the wall of the tank by 2'' GI pipes fixing in the concrete at casting time. | Nos | 4
1.2 | Steel ladder – Provide and fix from the ground to the tank top slab and duly painted to protect from rust. | Nos | 1
1.21 | Kiosk for tracks– Provide 2'' GI standpipe with plastic pipe near the tank. | Nos | 1
Sub-total A
B | PIPELINE WORKS
2 | Distribution network pipeline
2.1 | Supply of Ø 2" HDPE PN10 Class B 2000 m long Distribution network buried at 0.70 m below ground from the new shallow well to the new 25cum elevated tank inclusive with necessary fittings. | Lm | 1000
2.2 | Excavation of trench line for pipeline installation at the mean depth of 50cm x 0.30m width x 2000m long, incl. proper anchor beds all along the pipeline. | m3 | 225
2.3 | Provide and install Ø 2" HDPE PN10 Class B transmission pipe c/w all the necessary fittings and fix and protect the pipe with a bed and cover layer of silt sand compacted at 85 Proctor completely. | Lm | 500
2.4 | With the relicts of excavation backfill the trench completely. | m3 | 300
Sub-total B
C | SUBMERSIBLE PUMP AND ITS ANCILLARY SOLAR SYSTEM AND RISER PIPES
3 | Procure and fix complete solar panels and submersible pump with all their accessories
3.1 | Procure and install Grundfos SP9-52 400V 11kW 2'' Submersible pump (or approved equivalent) with 250m head and 192 l/m with water sensor (position to fix the pump at 160m/170m from the top). | unit | 1
3.2 | Procure and install Solar Panels 450Watts, Germany or CE-certified. | Nos | 20
3.4 | Procure and install Aluminum Mounting Structure frames –Imported standard not locally made frames with 30cmx30cm and 50cm depth plain concrete foundation. | Nos | 25
3.5 | Cable interconnection cables 6mm | Lm | 150
3.6 | Change Over switch 6A | Nos | 1
3.7 | Accessories (Cable tie, interconnection cables, MC4, cable connection set, etc.). | Unit | 1
3.8 | DC cable 16mm for solar (3 core / Three strings) | Lm | 159
3.9 | Cable 1x6mm DC | Lm | 40
3.1 | Complete earthen system & Accessories such as solar array grounding and inverter ground | Unit | 1
3.11 | Riser pipes– Ø 2" HDPE PN15 Class C inclusive with necessary fittings. | Pcs | 27
Sub-total C
D | CONSTRUCTION OF HEAVY GAUGE CHAIN-LINK FENCE FOR SOLAR PANELS AND CONSTRUCTION OF OPERATOR ROOM.
4 | Fencing solar panels with HEAVY GUAGE chain-link attached to 2" GI pipes posts using 3mm galvanized wire
4.1 | Supply and erect 2" GI pipes made 2m high posts (pillars) c/c 3m welded on the top Y posts and constructed on the bottom 30cmx 30cm and 50cm depth plain concrete foundation. | No | 20
4.2 | Supply and fix 2m high HEAVY GUAGE chain-link to posts anchoring with 3mm galvanized wire. Allow for securing the chain-link to a 12mm reinforcement bar welded at the base (bottom) and placed in a 10m thick and 30cm depth plain concrete foundation between every two the posts. | Lm | 40
4.3 | Supply and fix razor wire secured on the chain-link, at Y posts by binding wire and rolled approximately 600mm dia. | Lm | 40
4.5 | Procure and install 1mx2.1m steel door with 2 RCC columns of 10cmx1cmx2.20m | Nos | 1
Sub-total C
E | CATTLE AND CAMEL TROUGH
5 | Construction of 1 trough (internal dimension 8mx1mx0.40m) for cattle and camels complete with accessories
5.1 | Site clearance, leveling and clear unnecessary materials away direct from the site. | Sqm | 30
5.2 | Excavation foundation basement (8m x 3 x 0.5) m3 | Cum | 15
5.3 | 300mm thick stone hardcore filling well compacted and levelled, (10x3x0.3) m3 | Cum | 9
5.4 | 50mm thick sand blinding layer over hardcore (8 x 3 x 0.05) m3 | Cum | 3
5.5 | Cast 10mm lean concrete for the floor slab (1:3:6 mix ratio) -(10m x 3m x 0.1m) | Sqm | 1.5
5.6 | 150mm RCC slab with diameter 10mm iron bars c/c 15cm on both directions (8.3mx1.3mx0.20m) | Cum | 2.158
5.7 | 150mm RCC slab with diameter 10mm iron bars c/c 15cm on both directions (8.3m+1.m)0.15m*2 | Sqm | 1.116
5.8 | 50mm thick cement and sand floor screed at 1:3 mix (8 x 1) m2 | Sqm | 8
5.9 | External and internal plastering of 12mm thick cement and sand mix 1:4 with wood float finish. | Sqm | 14.88
5.1 | Apply external coat of whitewashing and distempering. | Sqm | 7.44
5.11 | Supply and fix 2'' GI pipe with T-section and heavy-duty tape to provide the pipe for two sections of animal troughs c/w 10m long 1'' pipe connecting to the system. | Unit | 1
Sub-total E
F | CONSTRUCTION OF 1 GOAT AND SHEEP WATERING TROUGH
6 | Supply and Construction of 1 trough (internal dimension 6mx1mx0.20m) for sheep and goats complete with accessories
6.1 | Site clearance, leveling and clear unnecessary materials away direct from the site | Sqm | 18
6.2 | Excavation foundation basement (8m x 3 x 0.5) m3 | Cum | 12
6.3 | 300mm thick stone hardcore filling well compacted and leveled, (8 x 3 x 0.3) m3 | Cum | 9
6.4 | 50mm thick sand blinding layer (1:4:8 mix) over the hardcore (8 x 3 x0.0.05) m3 | Cum | 1.2
6.5 | Cast 10mm lean concrete for the floor slab (1:3:6 mix ratio) -(8m x 3m x 0.1m). | Sqm | 2.4
6.6 | 150mm RCC slab with diameter 10mm iron bars c/c 15cm on both directions (6.3mX1.45mX0.20m). | Cum | 1.827
6.7 | 150mm thick RCC walls with diameter 10mm iron bars c/c 15cm on both directions (6.3m+1.m)0.15m*2+6.3*0.4*0.15). | Sqm | 0.816
6.8 | 50mm thick cement and sand floor screed at 1:3 mix (6 x 1) m2. | Sqm | 6
6.9 | External and internal plastering of 12mm thick cement and sand mix 1:4 with wood float finish. | Sqm | 9.62
6.1 | Apply external coat of whitewashing and distempering. | Sqm | 2.29
6.11 | Supply and fix 2'' GI pipe with T-section and heavy-duty tape to provide the pipe for two sections of animal trough c/w10m long 1'' pipe connecting to the system. | Unit | 1
Sub-total F
Grand Total
(CONTRACTOR) Name:…………………………………………………………………………………
Signature: …………………………………………………………………………………….............
Address: …………………………………………………………………………………….............
Tel No: ………………………………………………………………………………………….........
Date: ……………………………………………………………………………………………………
Stamp: