DETAILED MATERIAL SPECIFICATION OF incinerator.

All construction materials used for the renovation of Hayayabe MCH incinerator shall be new, of first quality, and free from defects. Cement shall be Ordinary Portland Cement (OPC),

while fine aggregate shall consist of clean river sand and coarse aggregate shall be hard, durable crushed stone. Concrete works shall include 150 mm thick compacted hardcore, 75 mm thick M25 concrete floor slab (1:1:2 mix), 100 mm thick reinforced concrete footings, 10 mm thick cement screed finish, and 170 × 250 mm reinforced concrete lintels constructed in accordance with the approved drawings. All concrete shall be properly mixed, placed, compacted, and cured to achieve the required strength and durability.

The medical waste incinerator shall be constructed using 110 mm thick refractory fire clay bricks for the combustion chamber walls and base, laid with heat-resistant refractory mortar. Fabricated steel components, including the loading door, ash door, and cover plate, shall be manufactured from 3 mm thick mild steel plates welded to

30 × 30 × 3 mm mild steel angle frames. The chimney shall consist of a 150 mm diameter × 3 mm thick mild steel pipe, complete with a 114 mm diameter × 3 mm thick chimney sleeve, heavy-duty steel hinges, and 25 × 25 mm secondary air inlet openings to ensure efficient combustion. All exposed steel surfaces shall receive anti-corrosion primer followed by approved oil-based paint.

The incinerator shelter shall be roofed with galvanized IBR corrugated iron sheets fixed to 50 × 50 mm steel purlins supported by engineered steel roof trusses with an approximate 22.5° roof pitch. The protective enclosure shall be constructed using 100 × 100 × 3 mm galvanized chain-link mesh fixed to 75 mm diameter steel pipe posts welded onto 200 × 200 mm steel base plates anchored in concrete foundations. The access gate shall measure 2000 × 750 mm, fabricated from steel framing with 32 mm diameter round bars, complete with heavy-duty hinges and locking devices. All materials shall be installed in strict accordance with the approved drawings and to the satisfaction of the Supervising Engineer

| Item | Material Type | Dimensions | Specification |
| --- | --- | --- | --- |
| Incinerator Wall | Fire Clay Brick | 110 mm thick | High-temperature refractory fire clay bricks for combustion chamber walls. |
| Combustion Chamber Base | Fire Clay Brick | As per drawing | Fire clay brick base laid level for high-temperature resistance. |
| Support Brickwork | Fire Clay Brick | 110 mm thick | Fire-resistant brickwork above combustion chamber. |
| Loading Door | Mild Steel Plate | 3 mm thick | Fabricated MS loading door welded to steel angle frame and finished with anti-rust paint. |
| Ash Door | Mild Steel Plate | 3 mm thick | Fabricated ash removal door complete with hinges and locking system. |
| Chimney Cover Plate | Mild Steel Plate | 3 mm thick | Steel cover plate welded to chimney support pipe. |
| Door Frame | Mild Steel Angle | 30 × 30 × 3 mm | Welded angle frame supporting loading and ash doors. |
| Chimney Support Frame | Mild Steel Angle | 30 × 30 × 3 mm | Angle frame welded to support chimney assembly. |
| Chimney vent Pipe | Mild Steel Pipe | Ø150 mm × 3 mm thick | Welded vertical exhaust chimney. |
| Chimney Sleeve | Mild Steel Pipe | Ø114 mm × 3 mm thick | Steel pipe fixed to chimney cover plate. |
| Hinges | Heavy-duty Mild Steel | Standard | Welded steel hinges for loading and ash doors. |
| RCC lintel support brick above | Concrete grade 20 | M20 1:1.5:3 |  |

DETAILED MATERIAL SPECIFICATION

Roof Structure (Section Drawing)

1. Timber Roof Trusses

Material

Well-seasoned, kiln-dried hardwood timber.

Timber shall be free from rot, termites, fungal attack, splits, excessive knots, and warping.

Moisture content shall not exceed 20%.

All timber shall be pressure-treated with an approved preservative before installation.

Members (as shown on drawing)

| Member | Size |
| --- | --- |
| Rafters | 120 × 60 mm (12 × 6 cm) hardwood |
| Purlins | 70 × 50 mm (7 × 5 cm) hardwood |
| Tie Beam | 100 × 50 mm hardwood (minimum) |
| Struts & Bracing | 100 × 50 mm hardwood |

Installation

Fabricate trusses to the dimensions shown on the drawings.

Fix members using 12 mm galvanized bolts with washers, galvanized nails, or steel connector plates as required.

Anchor trusses securely to the reinforced concrete ring beam using 12 mm galvanized holding-down bolts cast into the concrete.

Provide adequate diagonal bracing to ensure roof stability.

2. Roofing Sheets

Material

Corrugated Galvanized Iron (CGI) Roofing Sheets

Specification

Thickness: 28 Gauge (approximately 0.40 mm)

Pre-painted or hot-dip galvanized finish.

Zinc coating: Minimum Z275 or equivalent.

Factory-coated corrosion-resistant finish.

Colour: As approved by the Engineer.

Installation

Lay sheets starting from the leeward side.

Side lap: Minimum one corrugation.

End lap: Minimum 150 mm.

Fix each sheet to every purlin using self-drilling galvanized roofing screws with neoprene washers.

Install straight and aligned to prevent water leakage.

3. Fascia Board

Material

25 mm thick treated hardwood fascia board.

Finish

Sanded smooth.

Primed and painted with two coats of exterior weather-resistant paint.

Complete with brackets, stop ends, outlets, unions, and downpipes.

5. Reinforced Concrete Ring Beam

Material

Concrete Grade C20

Reinforcement

4Y12 longitudinal bars.

Y8 stirrups at 200 mm centres.

Concrete cover: 25 mm.

Specification

Ring beam shall be cast continuously around the building.

All reinforcement shall comply with BS 4449 or equivalent.

10. Ventilation

Provide high-level ventilation openings protected with galvanized steel insect mesh to maintain adequate airflow and reduce moisture accumulation. 150mm dia,3mm thick MS pipe chimney welded onto the chimney base plate

This specification aligns well with the rest of your MCH toilet section, including the timber roof trusses, 28-gauge CGI roof sheets, reinforced concrete ring beam, 100 mm reinforced concrete floor slab, and 300 mm compacted hardcore. It is suitable for inclusion in the technical specifications for the Hayayaabe MCH renovation project.

# TECHNICAL MATERIAL SPECIFICATIONS

## MCH DELIVERY WARD TOILET

(Based on Approved Section Drawing)

Item; Building Element; Material Specification; Installation / Workmanship Requirements. 1; Site Clearance; Remove vegetation, debris, and unsuitable materials from site.; Clear site completely and set out according to approved drawings.. 2; Excavation; Excavate to required depth and dimensions.; Trim, level and compact excavation base before foundation works.. 3; Foundation Concrete; Reinforced concrete Grade C25/30.; Place on 50 mm concrete blinding and compact using mechanical vibrator.. 4; Reinforcement; High Yield Steel Bars (Fy = 460 MPa) as shown on structural drawings.; Secure reinforcement with correct concrete cover and tie using binding wire.. 5; Construction Wall; 400 × 200 × 200 mm hollow concrete blocks.; Lay in 1:4 cement: sand mortar with 10 mm joints.. 6; Backfilling; Approved selected fill.; Place in 150 mm layers and compacted.. 7; Hardcore Filling; 300 mm thick well-graded crushed stone hardcore.; Compact in layers not exceeding 150 mm.. 8; Floor Slab; 100 mm reinforced concrete slab, Grade C25/30.and 150mm for septic tanks slab,; Reinforce with Ø12 bars @200 mm c/c each way as shown on drawing.. 9; Floor Finish; 40 mm cement: sand screed (1:3 mix).; Finish smooth and slope towards floor drain.. 10; Wall Construction; 400 × 200 × 200 mm hollow concrete blocks, minimum strength 7.5 MPa.; Lay in stretcher bond using 1:4 cement: sand mortar.. 11; Internal Wall Finish; 12 mm cement: sand plaster (1:4).; Steel trowel finish, ready for painting.. 12; External Wall Finish; 12 mm cement:sand plaster (1:4).; Sponge finish followed by exterior paint.. 13; Ring Beam; Reinforced concrete Grade C25/30 with reinforcement as detailed.; Cast continuously around walls to support roof.. 14; Roof Trusses; Treated hardwood timber trusses.; Timber shall be seasoned, pressure-treated against termites and securely anchored to ring beam.. 15; Rafters; 120 × 60 mm treated hardwood.; Fix to trusses using galvanized bolts or nails.. 16; Purlins; 70 × 50 mm treated hardwood.; Space evenly and securely fix to rafters.. 17; Roofing Sheets; 28-gauge pre-painted corrugated galvanized iron sheets.; Fix with galvanized self-drilling screws and neoprene washers; provide minimum one corrugation side lap and 150 mm end lap.. 18; Ridge Cap; Matching galvanized ridge cap.; Fix with roofing screws and seal against water penetration.. 19; Fascia Board; 25 mm treated hardwood fascia board.; Prime and paint with weather-resistant paint.. 20; Rainwater Goods; Heavy-duty PVC gutters with 100 mm diameter downpipes.; Install to fall towards outlets and discharge away from foundations.. 21; Ceiling (if applicable); 6 mm fiber cement board or PVC ceiling on galvanized framing.; Fix level with neat joints and access panels where required.. 22; Door; Hardwood frame, minimum 100 × 50 mm, seasoned and pressure-treated against termites and fungal attack,; Install plumb and ensure smooth operation.. 23 Door type; single-leaf solid core flush door.; The installation will Three (3) heavy-duty stainless steel butt hinges, 100 mm × 75 mm.; Install plumb and ensure smooth operation.. 24; Windows; 50x50 5mm clear aluminum glass, security mesh (5 cm spacing), 20×20×2 mm frame including mosquito net.. 25; Plumbing Pipes; PPR pipes for water supply and uPVC pipes for drainage.; Pressure-test water pipes and leak-test drainage before commissioning.. 26; Sanitary Fixtures; Vitreous China WC, wash hand basin, taps, floor trap, and accessories. long; Install complete with all fittings and connect to water supply and sewer system.. 27; Ventilation; 100mm UPVC High-level ventilation openings with galvanized insect mesh.; Provide permanent natural ventilation in accordance with approved drawings.. 28; Painting; Interior: acrylic emulsion paint. Exterior: weather-resistant acrylic paint.; Apply one coat primer and two finish coats over prepared surfaces.. 29; Water supply, drainage, sanitary fixtures, and roof.; Test all installations, rectify defects, clean the building, and hand over in good working condition..

### Applicable Standards

- Reinforcement: BS 4449

- Timber: BS 5268 or equivalent

- Roofing Sheets: ASTM A653 or equivalent galvanized steel standard

- Plumbing: BS EN 12056 and relevant local codes

This format is ready to be inserted directly into your Technical Specifications section and aligns with the construction details shown on your MCH toilet section drawing.

Electrical Wiring and Installation Specification

| Item | Specification |
| --- | --- |
| Electrical Wiring | 450/750 V PVC insulated, stranded copper conductor cables installed in heavy-duty PVC conduit, concealed within walls and ceilings. |
| Lighting Circuit | 1.5 mm² PVC insulated copper cable (Live, Neutral, and Earth). |
| Socket Outlet Circuit | 2.5 mm² PVC insulated copper cable (Live, Neutral, and Earth). |
| Main Power Supply | 6 mm² PVC insulated copper cable from the distribution board, or as determined by the approved electrical load calculations. |
| Conduit | 20 mm diameter heavy-duty rigid PVC conduit complete with approved fittings, bends, couplers, and junction boxes. |
| Switches | 10 A, one-gang, flush-mounted, moisture-resistant switches suitable for hospital sanitary facilities. |
| Socket Outlet | 13 A single switched socket outlet with earth connection, installed only at approved locations and at least 600 mm away from water sources. |
| Light Fittings | 18–20 W LED moisture-resistant ceiling luminaires with a minimum protection rating of IP65, suitable for wet and humid environments. |