## Shallow well
BOQ for Rehabilitation of Shallow Well with solar powered system
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE (USD) | AMOUNT (USD)
A | Preliminaries
1 | Demolish: Demolish existing shallow well apron and cart away of demolished materials | Ls | 1
B | Deepining Works
1 | Deepening of the shallow well up to an additional 5 m to reach good yield, costs should include disilting, and pumping of the water | M | 23.55
2 | Disposal of Excavated Material: Store the excavated material at least 5 meters away from the well location and curt away after completion of the construction. Some of The material Should later be used for backfilling and site levelling. | m3 | 23.55
E | Apron Construction
1 | Construct a 2.5m RC apron (50cm below GL and 85cm above GL) natural stone to apron in 1:3 sand/cement mortar finished with steel finished on one side. Rate to included mild all reinforcement at every alternate course | m3 | 6.4433
2 | Construct a 400x350mm thick Reinforced Concrete ring beam. Reinforced with 4D12mm steel bars main bars and 8mm @ 150mm intervals links, The price should include formworks. | m3 | 1.6705
3 | Construct a 150mm thick Reinforced cover slab Concrete with surface steel trowelled smooth. Use A142 BRC mesh for reinforcement. The price should include formworks | m3 | 0.7065
4 | 20 deg. Sloped ramp rubble stonework around the apron for water diversion. The ramp is 1m long from its edge to the side of the apron and 0.5m thick around the apron. | m3 | 2.1666
F | Finishing and Testing
1 | Disinfection of well: Disinfect the well with a chlorine solution (50mg/L concentration) to kill any harmful bacteria or microorganisms before water is drawn for use | Ls | 1
2 | Yield Testing: Monitor the yield by pumping the water for 6-12 hours and Monitor the recovery rate of the well to ensure it meets the required water demand. | Ls | 1
3 | Water Analysis: Analys the Water using field test kits; 2 water samples for each of the tests including Chemical, bacterial and Turbidity tests | Ls | 1
G | Branding Services
1 | Branding: Branding Services for PAH and the Donor logos. The branding is to be inscribed in wet plaster | Job | 1
Total of one shallow well rehabilitation cost
H | Solar Pannels
1 | 1.4 Kw Grundfos SQFlex centrifugal submersible pump (SQF 7-4N) and with Product No.: 98994902 with matching cut-off electrodes, & control Unit | Pcs | 1
2 | JA Solar JAM72D00 350-370/PR Monocrystalline or equivalent (Pmax= 550W, Voc= 47.28V, Vmp= 38.72V, Isc= 9.52A, Imp= 9.04A, Effeciency=18% at standard test conditions). Provide data sheets for any alternative offered. Note that the Solar panels will be installed in one (1) string. | Pcs | 8
3 | Solar Inverter (CIU 202 SQFlex). The controller should be enclosed in an adequate lockable safety box/cover to protect against weather and tampering. Provide proper ventilation of the inverter. | Pcs | 1
4 | Well prob sensor | Unit | 1
5 | PV Disconnect 1000-40-5 | Unit | 1
6 | Cable16 mm² 3-phase cable for power | m | 25
7 | Framed Solar Mounting structural steelwork; complete with and including all welded and bolted connections; and including one shop coat red oxide, zinc chromate, or similar and approved primer and 2 finishing coats of gloss oil paint after erection as Shown in the design and as directed by the Engineer. The tower to be 3m high on the lowest end. The tower to be encased in of 400x400x650mm reinforced concrete base pads | LS | 1
8 | Combiner Box | Pcs | 1
9 | Any other solar accessories and solar packages including wiring assessories for the solar panels and any other that may have not been explicitly covered in this BOQ. Including U/G Cables,Earthing etc | LS | 1
SUB -TOTAL: 2(Total of one shallow well rehabilitation cost)
| SUB -TOTAL 1 AND 2 |  |  |  | 0

## E.water tank
ELEVATED WATER TANK 9 METER HIGH
Boq of elevated water tank 9.00 meter high, 25M Capacity-in Afgoye District
Sr.No | Description | Unit | Quantity | Unit cost | Total amount
1 | Excavate for footing foudation wide 1.20 x 1.20 length x 1.5m deep commencing from ground level | M3 | 2.16
2 | Excavate foundation trench 0.5m wide x length 12.8m x1.55 depth commencing from ground below level | M3 | 9.92
3 | Lean concrete in 0.10m thick blinding layer (1:4:8 mix ) under the foundation wall & footing (12.8*0.4*.0.10) | M3 | 0.512
4 | Construction of RCC footing columns (1.2m wide x1.2m length x1.55m depth)4 with 4Y16 & 2Y14 rebars both way links with R8 @ 200mm c/c | M3 | 6.2
5 | Construction of stone masonry 0.4 wide x 12.8m length x 1.55m depth in cement & sand mortar 1:4 | M3 | 7.94
6 | Compacted hardcore and well blinded with approved blinding layer(4mx4mx 0.45m depth) | M2 | 7.2
7 | 0.2m base slab (1:2:4) reinforced with Y12 & Y12 rebars both way links with R8 @ 200mm c/c 12.8 x 0,4 x 0.20 | M3 | 1.28
8 | Construction of RCC columns ( 0.4x0.40 x 9 m high) 4 pcs at ratio (1:2:4) reinforced with Y16 & Y16 rebars both ways links with R8 @200mm c/c | M3 | 6.4
9 | Construction of RCC interm ring beam (1:2:4) reinforced with Y12 & Y12 rebars both ways links with R8 @200mm c/c (16*0.4*0.20)4 | M3 | 5.12
10 | Construction of RCC ring beam below bottom slab (1:2:4) reinforced with Y12 & Y12 rebars both ways links with R8 @200mm c/c | M3 | 1.28
11 | 0.2m bottom slab (1:2:4) with Y12 & Y12 rebars both ways links with R8 @200mm c/c inclusive and sleeves for inlet and outlet water pipes | M3 | 1.28
12 | Construction of RCC walls of water tank (1:2:4) reinforced with Y12 & Y12 rebars both ways links with R8 @200mm c/c (16m* 0.20* 2.) | M3 | 1.024
13 | Prepare and lay 20cm thick cement flooring with screed finished smooth cement slurry(3.2*3.2*.0.20)4 | M3 | 8.19
14 | 0.12m top slab (1:2:4) reinforced with Y10 rebars both ways links with R8 @200mm c/c inclusive of 600 x 500mm manhole cover and sleeves for inlet and outlet water pipes 12.8x0.12x0.4)4 | M3 | 2.46
15 | 25mm thick plaster and paint with two coats of white wash to all beams and columns & water tank | M2 | 82
16 | Paint two coats of emulsion paint to the internal and external walls, beams and columns | M2 | 28
17 | G.I pipe Ǿ1 1/2 inches | PCS | 1
18 | Elbow Ǿ 1 1/2 Inches | PCS | 3
19 | Union Ø2½ | Pcs | 3
20 | ValveØ2½ | Pcs | 2
21 | Nipples Ø2 inch | Pcs | 4
22 | Socket Ǿ 1 1/2 Inches | Pcs | 5
23 | Tee Ǿ1 1/2 Inches | Pcs | 4
24 | Reducer Ø2__1/2 inches | Pcs | 5
25 | Inlet & outlet water Taps with gate valves | Pcs | 2
26 | vissibility | Pcs | 1
27 | Install a ladder to the walk way platform up to the tank roof | L.S | 1
28 | Transportation of materials | Item | 1
Total of one elevated water tank

## Water kiosk
Construction of water caretaker room with Kiosks 3.00 m X 3.00 m
S/N | DESCRIPTION | UNIT | Quantity | Unit Price USD | Amount USD
1 | Clearing & preparation of site & removal of the site 3X 3 meter including cutting down & removal of top soil upto a depth of 150mm & disposal of rubbish out of the site as directed by the engineer | M2 | 9
2 | Excavation of foundation trench 12 m* 0.40* 0.80 m | M3 | 3.84
3 | Construction of foundation wall 12 m * 1.10 * 0.40 m | M3 | 5.76
4 | Construction of 20 cm thick lintel over the foundation wall | M3 | 0.96
5 | Construction of concrete block | M2 | 38.4
6 | Construction of 15 cm thick lintels in the middle & top | M3 | 0.96
7 | Plastering of internal/external walls of the building. | M2 | 76.8
8 | Construction of corrugated iron sheet with rafters,purlins & nails | M2 | 16
9 | Fixture of steel windows 1.0 m * 1.20 m with steel burglar protection | Pcs | 3
10 | Supply & fixture of steel door with inside & outside locks | Pcs | 1
11 | White wash | M2 | 76.8
12 | Plastic emulsion paint | M2 | 76.8
13 | Exterior steel railing on the front wall ( 2.50 m wide * 1.20 m high) | M2 | 3
14 | Fixture of facia board | L.m | 12
15 | Supply one chair & one table | Item | 1
16 | Supply & fix water taps with connection of verticle and Horizontal GI pipes(crosses,joints & other necesarry fittings | Pcs | 5
17 | Writing visibility logo | Item | 1
Sub-Total of one room
Construction of pipe line extension of 84 linear meter long
18 | Digging of foundation trench 84.00 m *0.50 m. * 0.4 m | M3 | 8.4
19 | Provide & Insert 2'' PVC. pipe with all necssary fitting(joints , elbows , reducers etc. from the main pipeline to the kiosk | L.m | 84
20 | Backfill the foundation trench , water & compact. | L.m | 84
Sub-Total
Grand total