## CA2&CA3_Latrines
Construction of new communal latrines for IDPs and Poor HHs
No | DESCRIPTION | UNIT | QTY | UNIT COST | TOTAL
1 | LANDSCAPING, PIT EXCAVATION AND LINING
1.1 | Excavation of pit measuring 2.3m width x 2.3m length x 2.5m depth | m³ | 13.225 |  | 0
1.2 | Stone masonry for the septic tank walling (2.3m x 2.3m x 2.5m) | m³ | 7.6 |  | 0
1.3 | 100 mm Reinforced concrete pit cover (6mm reinforcement steel). | m³ | 0.2 |  | 0
| SUBTOTAL 1 |  |  |  | 0
2 | SUPER STRUCTURE (WALLS OF TIMBER AND IRON SHEETS)
2.1 | Assorted Timber for wall structures 80mm x 40mm | m | 34 |  | 0
2.2 | Walling Iron sheets 1.5 m length x 1.5 m width 3m high. | pcs | 7 |  | 0
2.3 | Nails | kg | 2 |  | 0
2.4 | Door with secure lockable from outside and inside | pcs | 1 |  | 0
2.5 | 100mm Vent pipe with fly screen cork. | m | 2 |  | 0
| SUBTOTAL 2 |  |  |  | 0
3 | FLOOR FOUNDATION, PIT FINISHING AND DELIVERY PIPES
3.1 | Foundation walling around perimeter of the latrine and drop hole construction using 200mm x 400mm hollow blocks. | m² | 1.5 |  | 0
3.2 | Concrete Slab of the toilet. | m³ | 0.1 |  | 0
3.3 | Delivery pipe of 160mm. | m | 1.5 |  | 0
3.4 | SUBTOTAL 3 |  |  |  | 0
4 | ROOFING & PAINTING
4.1 | Corrugated iron sheets for roof of 1.7m x 1.7m. | pcs | 2 |  | 0
4.2 | Assorted timber 50mmx50mm. | m | 15 |  | 0
4.3 | Nails | kg | 2 |  | 0
| SUBTOTAL 4 |  |  |  | 0
5 | OTHERS
5.1 | Fabrication and installation of hand washing jerrycan with wood supporting element. | pcs | 1 |  | 0
5.2 | Visibilty board on each toilet. | pcs | 1 |  | 0
| SUBTOTAL 5 |  |  |  | 0
COST FOR CONSTRUCTION OF ONE NEW NON-DISABLE COMMUNAL LATRINE |  |  |  |  | 0
Construction of new communal latrines for people with disabilities
No | DESCRIPTION | UNIT | QTY | UNIT COST | TOTAL
1 | LANDSCAPING, PIT EXCAVATION AND LINING
1.1 | Excavation of pit measuring 2.3m width x 2.3m length x 2.5m depth | m³ | 13.225 |  | 0
1.2 | Stone masonry for the septic tank walling (2.3m x 2.3m x 2.5m) | m³ | 7.6 |  | 0
1.3 | 100 mm Reinforced concrete pit cover (6mm reinforcement steel). | m³ | 0.2 |  | 0
| SUBTOTAL 1 |  |  |  | 0
2 | SUPER STRUCTURE (WALLS OF TIMBER AND IRON SHEETS)
2.1 | Assorted Timber for wall structures size of 80mm x 40mm. | m | 34 |  | 0
2.2 | Walling Iron sheets 2 m length x 2 m width 3m high. | pcs | 7 |  | 0
2.3 | Nails | kg | 2 |  | 0
2.4 | Door with secure lockable from outside and inside | pcs | 1 |  | 0
2.5 | 100mm Vent pipe with fly screen cork. | m | 2 |  | 0
| SUBTOTAL 2 |  |  |  | 0
3 | FLOOR FOUNDATION, PIT FINISHING AND DELIVERY PIPES
3.1 | Foundation walling around perimeter of the latrine and drop hole construction using 200mm x 400mm hollow blocks. | m² | 1.5 |  | 0
3.2 | Pour 80mm concrete slab of the toilet. | m³ | 0.1 |  | 0
3.3 | Delivery pipe of 160mm. | m | 1.5 |  | 0
3.4 | SUBTOTAL 3 |  |  |  | 0
4 | ROOFING & PAINTING
4.1 | Corrugated iron sheets for roof of 2.3m x 2.3m. | pcs | 2 |  | 0
4.2 | Assorted timber 50mmx50mm. | m | 15 |  | 0
4.3 | Nails | kg | 2 |  | 0
| SUBTOTAL 4 |  |  |  | 0
5 | OTHERS
5.1 | Fabrication and installation of hand washing jerrycan with wood supporting element. | pcs | 1 |  | 0
5.2 | Provision of an access ramp of size 1000 x 2250mm wide with steel handrails. | Lsm | 1 |  | 0
5.3 | Visibilty board on each toilet. | pcs | 1 |  | 0
| SUBTOTAL 5 |  |  |  | 0
COST FOR CONSTRUCTION OF ONE NEW DISABLE COMMUNAL LATRINE |  |  |  |  | 0

## CA9_Gargaar Borehole
GARGAAR Borehole Upgrading with Solar pumping system with submersible pump, 1800m Water extension, 2 water kiosk.
BOREHOLE SOLAR WATER PUMPING SYSTEM WITH SUBMERSIBLE PUMP
S/N | Item description | Unit | Quantity | Unit price | Total
1 | Solar Pump Inverter 45KW Controller/pump Inverter Input DC & AC Output 380VAC 3Phase 50Hz with disconnected all solar combiners American or European made. | Item | 1 |  | 0
2 | Supply and installation of PV Module, 545w monocrystalline, junction box, cable. | Nr | 80 |  | 0
3 | Supply and install AC Pump Cable 16X4mm2. 4 core UV Resistant. | m | 150 |  | 0
4 | 25mm PVC pipe for protection of pump cable underground between borehole to generator room | pcs | 10 |  | 0
5 | Supply and installation of PV/ cable of 6mm2 (Red and Black) | pcs | 100 |  | 0
6 | Well probe sensor | Unit | 1 |  | 0
7 | Well probe sensor cable cable 2.5mm | m | 150 |  | 0
8 | Manual change over switch. | pc | 1 |  | 0
9 | Surge Protector | Unit | 1 |  | 0
10 | PV Combiner 1000V_125A_4 ways | Unit | 1 |  | 0
11 | Supply and installation of Earthing Wire 6sqmm | m | 50 |  | 0
12 | Water meter 3" for borehole pipe. | Unit | 1 |  | 0
13 | Electric Float switch connected to the solar system. | Unit | 1 |  | 0
14 | Supply and Install the Solar Support of mounting aluminum ground mounting structures lowest side of the structure to be 1metre tilting at 15degrees structure aluminium frame with complete mid and end clamps for all the 80PCs of the Solar Pannels (80pcs of 565W) the structure should have a proper concrete footings, (according to the site requirements and supervisor Engineer instructions) The concrete structure will be made of square hollow Aluminium anchored to the RC base in 1000 mm deep hole 500 mm x 500mm.). 500mm below ground floor and 500mm above ground floor. | Unit | 80 |  | 0
15 | Supply and installation of solar accessories and, internal wiring sundries, sensors, testing and commissioning of solar system and training the operator with basic needed knowledge. | Lot | 1 |  | 0
16 | Pull out old pipes and supply and install new 3 Inch uPVC Column Pipes 3” Water Pump Pipes (each pipe is 3meter) with all accessories. | Pcs | 42 |  | 0
17 | Pull out old Submersible pump and supply and install new American or European made Submersible pump of 30 KW with Maximum head of 200m the pump must be have minumum 20 m³/h | Pc | 1 |  | 0
18 | Splicing joint between the cable and the submersible pump with Gum | pcs | 2 |  | 0
19 | Visibility Board | Lsm | 1 |  | 0
TOTAL BOREHOLE SOLAR WATER PUMPING SYSTEM WITH SUBMERSIBLE PUMP |  |  |  |  | 0
CONSTRUCTION OF OPEN WATER KIOSK WITH 6 FAUCETS.
ITEM | ITEM DESCRIPTION | UNIT | Qty | RATE | AMOUNT
Excavation and Earthwork
1 | Excavate in soft material for foundation trenches not exceeding 250mm deep starting from stripped level | m3 | 2.4 |  | 0
| construction of water kiosk foundation using 200mm concrete hollow blocks with Cement mortar 1:6 (1 cement :6 coarse sand). | m2 | 5 |  | 0
Selected filling
2 | 250mm Thick hardcore filling compacted in layers not exceeding 150mm deep and well watered. | m3 | 2.4 |  | 0
3 | 50mm Thick quarry dust blinding to surfaces of hardcore (Measured Separately) | m2 | 0.5 |  | 0
Concrete work and Construction
Plain Concrete Class 15 / (1:3:6)
4 | 50 mm Thick slab on top of the laid hardcore. | m3 | 6 |  | 0
5 | 50mm thick concrete apron and drain channel | m3 | 1.7 |  | 0
6 | Construction of water kiosk wall using 200mm concrete hollow blocks with Cement mortar 1:6 (1 cement :6 coarse sand). | m2 | 5.5 |  | 0
Vibrated reinforced concrete class 25/20 with minimum cube crushing strength of 25N/mm² at 28 days
7 | 200mm 20/20 (1:2:4) RCC Capping. | m³ | 0.1 |  | 0
Mesh reinforcement ; B.S. 4483 ref A142 weighing 2.22 kgs per square meter including bends, tying wire and spacing blocks
8 | Fabric mesh reinforcement to ground floor slab | m2 | 12 |  | 0
Finishes
9 | Plaster (to wall, floor, etc) with cement and sand (1:6) mortar including rounding off or chamfering corners as directed and raking out joints including throating, nosing and drip course. | m² | 13 |  | 0
10 | Finishing wall with 100%Premium acrylic emulsion paint of approved brand and manufacture on wall surface, content including scraping and preparing the surface thoroughly, removing of dust etc all complete as permanufacturer's specification and direction of the site engineer. | m² | 13 |  | 0
Piping System
Supply, laying, test and commission the following:- PIPEWORK AND FITTINGS including All Joint Pipe Fittings all as required in the pipework installation. (elbows, nipples, sockets, gate valves, reducers, Tee PVC pipes, etc.)
11 | Excavate trench in all materials include for joint holes, trimming sides and preparing trench bottom, backfill with part of the materials and compact. Depth of excavation 0.5m and width not less than 0.4mm. | m³ | 3 |  | 0
12 | Backfilling either with insitu material or imported selected granular material for pipe surrounds and bedding as specified by the engineer. | m³ | 3 |  | 0
13 | 2 inch UPVC Pipe (High Preasure Pipe) Class C | m | 30 |  | 0
14 | Ditto but 1 inch | m | 20 |  | 0
15 | Taps 1" peglar | Nr | 6 |  | 0
16 | Gate valve 1" | Nr | 2 |  | 0
Soak away pit:
17 | Excavate (1000mm Diameter and 1500mm depth) soak pit, fill with granular material with high absorption capacity as shown in the drawing. | m3 | 1.2 |  | 0
Vibrated reinforced concrete class 25/20 with minimum cube crushing strength of 25N/mm² at 28 days
18 | 1100mm dia 75mm thick (1:2:4) soak pit cover slab. | No | 1 |  | 0
19 | Visibility board | Item | 1 |  | 0
TOTAL FOR CONSTRUCTION OF ONE WATER KIOSK |  |  |  |  | 0
200m EXTENSION PIPE TO WATER KIOSKS
ITEM | ITEM DESCRIPTION | UNIT | QTY | RATE | AMOUNT
1 | EARTHWORKS
1.1 | Excavate trench in all materials include for joint holes, trimming sides and preparing trench bottom, backfill with part of the materials and compact. Depth of excavation 0.3m width and 0.5m depth. | m³ | 72 |  | 0
1.2 | Backfilling either with insitu material or imported selected granular material for pipe surrounds and bedding as specified by the engineer. | m³ | 72 |  | 0
| SUBTOTAL 1 |  |  |  | 0
2 | PIPE WORK - PIPES
Supply, laying, test and commission the following:- PIPEWORK AND FITTINGS including All Joint Pipe Fittings all as required in the pipework installation. (elbows, nipples, sockets, gate valves, reducers, Tee PVC pipes, etc.)
2.1 | 3 inch UPVC Pipe (High Preasure Pipe) Class C from borehole to the camp | m | 180 |  | 0
2.2 | 2 inch UPVC Pipe (High Preasure Pipe) Class C from camps to the water kiosks | m | 20 |  | 0
| SUBTOTAL 2 |  |  |  | 0
TOTAL OF 1800m EXTENSION PIPE TO WATER KIOSK |  |  |  |  | 0
TOTAL OF REHABILITATION OF GARGAAR BOREHOLE |  |  |  |  | 0